## EAI RUL Assumptions
2030 Closure Assumed
Emission Unit | SO2 Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | WFGD | 401.82 | 136.1626 | 36.55 | 173.9727 | 9104 | 19109.4785
| DGFD | 377.69 | 127.9858 | 9.36 | 138.3479 | 8684 | 15931.3521
| Enhanced DSI | 335.58 | 76.5193 | 29.16 | 106.4503 | 6792 | 15672.8903
| DSI | 175 | 39.9037 | 16.6 | 56.9159 | 2587 | 22000.7337
Unit 2 | WFGD | 401.82 | 136.1626 | 36.55 | 173.9727 | 9786 | 17777.7122
| DGFD | 377.69 | 127.9858 | 9.36 | 138.3479 | 9342 | 14809.2337
| Enhanced DSI | 335.58 | 76.5193 | 29.16 | 106.4503 | 7347 | 14488.9439
| DSI | 175 | 39.9037 | 16.6 | 56.9159 | 2914 | 19531.8799
Units 1 and 2 averaged | WFGD | [5 empty] | 18443.5954
| DGFD | [5 empty] | 15370.2929
| Enhanced DSI | [5 empty] | 15080.9171
| DSI | [5 empty] | 20766.3068
Emission Unit | NOx Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | SCR | 186.32 | 63.1373 | 3.42 | 67.0429 | 2267 | 29573.3844
| SNCR | 8.75 | 2.9651 | 6.53 | 9.5643 | 690 | 13861.3614
Unit 2 | SCR | 186.32 | 63.1373 | 3.42 | 67.0429 | 1961 | 34188.0991
| SNCR | 8.75 | 2.9651 | 6.53 | 9.5643 | 298 | 32095.0985
Unit 1 and 2 averaged | SCR | [5 empty] | 31880.7417
| SNCR | [5 empty] | 22978.2299
CRF (2030 closure)
Equipment | Life Expectancy |  | Life Expectancy Reference |  | RUL | 7%
WFGD | 30 | years | EPA FIP AR TSD |  | 3.42 | 0.33886 | Calculated based on formula below
DGFD | 30 | years | EPA FIP AR TSD |  | 3.42 | 0.33886 | Calculated based on formula below
Enhanced DSI | 30 | years | EPA FIP OK TX TSD |  | 5.42 | 0.22802 | Calculated based on formula below
DSI | 30 | years | EPA FIP OK TX TSD |  | 5.42 | 0.22802 | Calculated based on formula below
SCR | 30 | years | Equipment Life Expectancy from Control Cost Manual |  | 3.42 | 0.33886 | Calculated based on formula below
SNCR | 20 | years | Equipment Life Expectancy from Control Cost Manual |  | 3.42 | 0.33886 | Calculated based on formula below
FGD & NOx strategies
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.33886
| interest |  | 0.07 |  | interest rate
| n (remaining useful life or RUL) |  | 3.42
DSI Strategies
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.22802
| interest |  | 0.07 |  | interest rate
| n (remaining useful life or RUL) |  | 5.42
Note on F37: Author<*>: Changing this changed most of the numbers above; check SIP references to this table

## EAI Equipment Life Assumptions
Equipment Life Sensitivity Calculations
Emission Unit | SO2 Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | WFGD | 401.82 | 32.3812 | 36.55 | 69.4341 | 9104 | 7626.7713
| DGFD | 377.69 | 30.4367 | 9.36 | 40.087 | 8684 | 4616.1931
| Enhanced DSI | 335.58 | 27.0432 | 29.16 | 56.6132 | 6792 | 8335.2802
| DSI | 175 | 14.1026 | 16.6 | 30.9266 | 2587 | 11954.6254
Unit 2 | WFGD | 401.82 | 32.3812 | 36.55 | 69.4341 | 9786 | 7095.251
| DGFD | 377.69 | 30.4367 | 9.36 | 40.087 | 9342 | 4291.0534
| Enhanced DSI | 335.58 | 27.0432 | 29.16 | 56.6132 | 7347 | 7705.6245
| DSI | 175 | 14.1026 | 16.6 | 30.9266 | 2914 | 10613.1146
Unit 1 and 2 averaged | WFGD | [5 empty] | 7361.0111
| DGFD | [5 empty] | 4453.6233
| Enhanced DSI | [5 empty] | 8020.4524
| DSI | [5 empty] | 11283.87
Emission Unit | NOx Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | SCR | 186.32 | 15.0149 | 3.42 | 18.5694 | 2267 | 8191.1569
| SNCR | 8.75 | 0.82594 | 6.53 | 7.4096 | 690 | 10738.5571
Unit 2 | SCR | 186.32 | 15.0149 | 3.42 | 18.5694 | 1961 | 9469.3283
| SNCR | 8.75 | 0.82594 | 6.53 | 7.4096 | 298 | 24864.4442
Unit 1 and 2 average | SCR | [5 empty] | 8830.2426
| SNCR | [5 empty] | 17801.5006
CRF
Equipment | Life Expectancy |  | Life Expectancy Reference |  | RUL | 7%
WFGD | 30 | years | EPA FIP AR TSD |  |  | 0.080586 | Calculated based on formula below
DGFD | 30 | years | EPA FIP AR TSD |  |  | 0.080586 | Calculated based on formula below
Enhanced DSI | 30 | years | EPA FIP OK TX TSD |  |  | 0.080586 | Calculated based on formula below
DSI | 30 | years | EPA FIP OK TX TSD |  |  | 0.080586 | Calculated based on formula below
SCR | 30 | years | Equipment Life Expectancy from Control Cost Manual |  |  | 0.080586 | Calculated based on formula below
SNCR | 20 | years | Equipment Life Expectancy from Control Cost Manual |  |  | 0.094393 | Calculated based on formula below
| FGD & SCR strategies | [5 empty] | SNCR
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.080586 |  |  |  | CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.094393
| interest |  | 0.07 |  | interest rate |  | interest | 0.07
| n (remaining useful life or RUL) |  | 30 |  |  |  | n (remaining useful life or RUL) | 20
DSI Strategies
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.080586
| interest |  | 0.07 |  | interest rate
| n (remaining useful life or RUL) |  | 30

## EAI RUL Sensitivity
Remaining Useful Life Sensitivity Calculations
Emission Unit Type | 98th Percentile
EGU Boiler | 5086
Emission Unit | SO2 Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | DGFD | 377.69 | 45.1909 | 9.36 | 54.9489 | 8684 | 6327.604
Unit 2 | DGFD | 377.69 | 45.1909 | 9.36 | 54.9489 | 9342 | 5881.9217
Units 1 & 2 averaged | DGFD | [5 empty] | 6104.7628
Equipment | Life Expectancy |  | 7%
DGFD | 13 | years | 0.11965
SIP Submission | Estimated EPA Approval Date | Estimated Compliance Date | Cost-Effective if Operate On or After
2021-07-31 | 2022-07-31 | 2027-07-31 | 2040-07-31
2021 | 2022 | 2027 | 2040

## CEPCI Index
Year (n) | CEPCI Index Value | Cost Index Ratio (Value2019/Valuen)
1998 | 389.5 | 1.5597
1999 | 390.6 | 1.5553
2000 | 394.1 | 1.5415
2001 | 394.3 | 1.5407
2002 | 395.6 | 1.5356
2003 | 402 | 1.5112
2004 | 444.2 | 1.3676
2005 | 468.2 | 1.2975
2006 | 499.6 | 1.216
2007 | 525.4 | 1.1563
2008 | 575.4 | 1.0558
2009 | 521.9 | 1.164
2010 | 550.8 | 1.1029
2011 | 585.7 | 1.0372
2012 | 584.6 | 1.0392
2013 | 567.2 | 1.0711
2014 | 576.1 | 1.0545
2015 | 556.8 | 1.0911
2016 | 541.7 | 1.1215
2017 | 567.5 | 1.0705
2018 | 603.1 | 1.0073
2019 | 607.5 | 1