## Read Me
Air Pollution Control Cost Estimation Spreadsheet
For Selective Non-Catalytic Reduction (SNCR)
U.S. Environmental Protection Agency
Air Economics Group
Health and Environmental Impacts Division
Office of Air Quality Planning and Standards
(March 2021)
This spreadsheet allows users to estimate the capital and annualized costs for installing and operating a Selective Non-Catalytic Reduction (SNCR) control device. SNCR is a post-combustion control technology for reducing NOx emissions by injecting an ammonia-base reagent (urea or ammonia) into the furnace at a location where the temperature is in the appropriate range for ammonia radicals to react with NOx to form nitrogen and water.
The calculation methodologies used in this spreadsheet are those presented in the U.S. EPA's Air Pollution Control Cost Manual. This spreadsheet is intended to be used in combination with the SNCR chapter and cost estimation methodology in the Control Cost Manual. For a detailed description of the SNCR control technology and the cost methodologies, see Section 4, Chapter 1 of the Air Pollution Control Cost Manual (as updated April 2019). A copy of the Control Cost Manual is available on the U.S. EPA's "Technology Transfer Network" website at: https://www.epa.gov/economic-and-cost-analysis-air-pollution-regulations/cost-reports-and-guidance-air-pollution.
The spreadsheet can be used to estimate capital and annualized costs for applying SNCR, and particularly to the following types of combustion units:
| (1) | Coal-fired utility boilers with full load capacities greater than or equal to 25 MW.
| (2) | Fuel oil- and natural gas-fired utility boilers with full load capacities greater than or equal to 25 MW.
| (3) | Coal-fired industrial boilers with maximum heat input capacities greater than or equal to 250 MMBtu/hour.
| (4) | Fuel oil- and natural gas-fired industrial boilers with maximum heat input capacities greater than or equal to 250 MMBtu/hour.
The methodology used in this spreadsheet is based on the U.S. EPA Clean Air Markets Division (CAMD)'s Integrated Planning Model (IPM version 6). The size and costs of the SNCR are based primarily on four parameters: the boiler size or heat input, the type of fuel burned, the required level of NOx reduction, and the reagent consumption. This approach provides study-level estimates (±30%) of SNCR capital and annual costs. Default data in the spreadsheet is taken from the SNCR Control Cost Manual and other sources such as the U.S. Energy Information Administration (EIA). The actual costs may vary from those calculated here due to site-specific conditions, such as the boiler configuration and fuel type. Selection of the most cost-effective control option should be based on a detailed engineering study and cost quotations from system suppliers. For additional information regarding the IPM, see the EPA Clean Air Markets webpage at http://www.epa.gov/airmarkets/power-sector-modeling. The Agency wishes to note that all spreadsheet data inputs other than default data are merely available to show an example calculation.
Instructions
Step 1: Please select on the Data Inputs tab and click on the Reset Form button. This will reset the NSR, plant elevation, estimated equipment life, desired dollar year, cost index (to match desired dollar year), annual interest rate, unit costs for fuel, electricity, reagent, water and ash disposal, and the cost factors for maintenance cost and administrative charges. All other data entry fields will be blank.
Step 2: Select the type of combustion unit (utility or industrial) using the pull down menu. Indicate whether the SNCR is for new construction or retrofit of an existing boiler. If the SNCR will be installed on an existing boiler, enter a retrofit factor equal to or greater than 0.84. Use 1 for retrofits with an average level of difficulty. For more difficult retrofits, you may use a retrofit factor greater than 1; however, you must document why the value used is appropriate.
Step 3: Select the type of fuel burned (coal, fuel oil, and natural gas) using the pull down menu. If you selected coal, select the type of coal burned from the drop down menu. The NOx emissions rate, weight percent coal ash and NPHR will be pre-populated with default factors based on the type of coal selected. However, we encourage you to enter your own values for these parameters, if they are known, since the actual fuel parameters may vary from the default values provided.
Step 4: Complete all of the cells highlighted in yellow. As noted in step 1 above, some of the highlighted cells are pre-populated with default values based on 2016 data. Users should document the source of all values entered in accordance with what is recommended in the Control Cost Manual, and the use of actual values other than the default values in this spreadsheet, if appropriately documented, is acceptable. You may also adjust the maintenance and administrative charges cost factors (cells highlighted in blue) from their default values of 0.015 and 0.03, respectively. The default values for these two factors were developed for the CAMD Integrated Planning Model (IPM). If you elect to adjust these factors, you must document why the alternative values used are appropriate.
Step 5: Once all of the data fields are complete, select the SNCR Design Parameters tab to see the calculated design parameters and the Cost Estimate tab to view the calculated cost data for the installation and operation of the SNCR.

## Data Inputs
Data Inputs
Enter the following data for your combustion unit:
Is the combustion unit a utility or industrial boiler? |  |  |  | What type of fuel does the unit burn?
Is the SNCR for a new boiler or retrofit of an existing boiler?
Please enter a retrofit factor equal to or greater than 0.84 based on the level of difficulty. Enter 1 for projects of average retrofit difficulty. |  |  | 1
Complete all of the highlighted data fields: | [12 empty] | 2 | Utility | New Construction | 3
|  |  |  | Provide the following information for coal-fired boilers: | [9 empty] | Industrial | Retrofit
| What is the MW rating at full load capacity (Bmw)? | 558 | MW | Type of coal burned: | [12 empty] | SO2 Emission Rate (lbs SO2/MMBtu) = | 0.92907
[14 empty] | < 3lb/MMBtu | Bituminous |  | SO2 Emission Rate | 2
| What is the higher heating value (HHV) of the fuel? | 8826 | Btu/lb | Enter the sulfur content (%S) = |  |  | 0.41 | percent by weight |  |  |  |  | 2 | ≥ 3lb/MMBtu | Sub-Bituminous | 3
| *HHV value of 8826 Btu/lb is a default value. See below for data source. Enter actual HHV for fuel burned, if known. |  |  | or Select the appropriate SO2 emission rate: | [9 empty] | Not Applicable | Lignite
| What is the estimated actual annual MWh output? | 2797891.9233 | MWh |  | *The sulfur content of 0.41% is a default value. See below for data source. Enter actual value, if known. | [9 empty] | Coal blend
|  |  |  | Ash content (%Ash): |  |  | 5.84 | percent by weight | [6 empty] | Not Applicable
| Is the boiler a fluid-bed boiler? |  |  |  | *The ash content of 5.84% is a default value. See below for data source. Enter actual value, if known. | [8 empty] | Coal
|  |  |  | For units burning coal blends: | [8 empty] | 2 | Fuel Oil
| Enter the net plant heat input rate (NPHR) | 10 | MMBtu/MW |  | Note: The table below is pre-populated with default values for HHV, %S, %Ash and cost. Please enter the actual values for these parameters in the table below. If the actual value for any parameter is not known, you may use the default values provided. | [8 empty] | Natural Gas
Coal Blend Composition Table
[7 empty] | Fraction in Coal Blend | %S | %Ash | HHV (Btu/lb) | Fuel Cost ($/MMBtu)
| If the NPHR is not known, use the default NPHR value: | Fuel Type | Default NPHR |  | Bituminous |  | 0 | 1.84 | 9.23 | 11841 | 2.4 |  |  |  | 10500
|  | Coal | 10 MMBtu/MW |  | Sub-Bituminous |  | 0 | 0.41 | 5.84 | 8826 | 1.89
|  | Fuel Oil | 11 MMBtu/MW |  | Lignite |  | 0 | 0.82 | 13.6 | 6626 | 1.74
|  | Natural Gas | 8.2 MMBtu/MW
[5 empty] | Please click the calculate button to calculate weighted values based on the data in the table above. | [7 empty] | 3 | Yes
[13 empty] | Note: If P25= Yes, then BTF = 0.75 for fluid bed boilers; Else BTF=1 | No
Enter the following design parameters for the proposed SNCR:
| Number of days the SNCR operates (tSNCR) | 288 | days |  | Plant Elevation |  | 250 | Feet above sea level
| Number of days the boiler operates (tplant) | 288 | days
| Inlet NOx Emissions (NOxin) to SNCR | 0.186 | lb/MMBtu
| Oulet NOx Emissions (NOxout) from SNCR | 0.18 | lb/MMBtu
| Estimated Normalized Stoichiometric Ratio (NSR) | 1.05
| Concentration of reagent as stored (Cstored) | 29 | Percent
| Density of reagent as stored (ρstored) | 56 | lb/ft3
| Concentration of reagent injected (Cinj) | 10 | percent |  |  | Densities of typical SNCR reagents:
| Number of days reagent is stored (tstorage) | 14 | days |  |  | 50% urea solution |  | 71 | lbs/ft3
| Estimated equipment life | 20 | Years |  |  | 29.4% aqueous NH3 |  | 56 | lbs/ft3 |  |  |  | 1 | Urea
[13 empty] | 2 | Ammonia
Select the reagent used
Enter the cost data for the proposed SNCR:
| Desired dollar-year | 2019
| CEPCI for 2019 | 607.5 | Enter the CEPCI value for 2019 | 541.7 | 2016 CEPCI |  | CEPCI = Chemical Engineering Plant Cost Index
| Annual Interest Rate (i) | 7 | Percent
| Fuel (Costfuel) | 1.89 | $/MMBtu*
| Reagent (Costreag) | 0.293 | $/gallon for a 29 percent solution of ammonia
| Water (Costwater) | 0.00417 | $/gallon*
| Electricity (Costelect) | 0.0361 | $/kWh*
| Ash Disposal (for coal-fired boilers only) (Costash) | 48.8 | $/ton*
Note: The use of CEPCI in this spreadsheet is not an endorsement of the index, but is there merely to allow for availability of a well-known cost index to spreadsheet users. Use of other well-known cost indexes (e.g., M&S) is acceptable.
Maintenance and Administrative Charges Cost Factors:
0.015
| Maintenance Cost Factor (MCF) = | 0.015
| Administrative Charges Factor (ACF) = | 0.03
Data Sources for Default Values Used in Calculations:
| Data Element | Default Value | Sources for Default Value |  |  |  |  | If you used your own site-specific values, please enter the value used and the reference source . . . |  |  |  | Recommended data sources for site-specific information
| Reagent Cost | $0.293/gallon of 29% Ammonia | U.S. Geological Survey, Minerals Commodity Summaries, January 2017 (https://minerals.usgs.gov/minerals/pubs/commodity/nitrogen/mcs-2017-nitro.pdf | [8 empty] | Check with reagent vendors for current prices.
| Water Cost ($/gallon) | 0.00417 | Average water rates for industrial facilities in 2013 compiled by Black & Veatch. (see 2012/2013 "50 Largest Cities Water/Wastewater Rate Survey." Available at http://www.saws.org/who_we_are/community/RAC/docs/2014/50-largest-cities-brochure-water-wastewater-rate-survey.pdf. | [8 empty] | Plant's utility bill or Black & Veatch's "50 Largest Cities Water/Wastewater Rate Survey." Available at http://www.saws.org/who_we_are/community/RAC/docs/2014/50-largest-cities-brochure-water-wastewater-rate-survey.pdf. .
| Electricity Cost ($/kWh) | 0.0361 | U.S. Energy Information Administration. Electric Power Annual 2016. Table 8.4. Published December 2017. Available at: https://www.eia.gov/electricity/annual/pdf/epa.pdf. | [8 empty] | Plant's utility bill or use U.S. Energy Information Administration (EIA) data for most recent year. Available at http://www.eia.gov/electricity/data.cfm#sales.
| Fuel Cost ($/MMBtu) | 1.89 | U.S. Energy Information Administration. Electric Power Annual 2016. Table 7.4. Published December 2017. Available at: https://www.eia.gov/electricity/annual/pdf/epa.pdf. | [8 empty] | Check with fuel supplier or use U.S. Energy Information Administration (EIA) data for most recent year. Available at http://www.eia.gov/electricity/data/eia923/.
| Ash Disposal Cost ($/ton) | 48.8 | Waste Business Journal. The Cost to Landfill MSW Continues to Rise Despite Soft Demand. July 11, 2017. Available at: http://www.wastebusinessjournal.com/news/wbj20170711A.htm. | [8 empty] | Use plant data or use Waste Business Journal. The Cost to Landfill MSW Continues to Rise Despite Soft Demand. July 11, 2017. Available at: http://www.wastebusinessjournal.com/news/wbj20170711A.htm.
| Percent sulfur content for Coal (% weight) | 0.41 | Average sulfur content based on U.S. coal data for 2016 compiled by the U.S. Energy Information Administration (EIA) from data reported on EIA Form EIA-923, Power Plant Operations Report. Available at http://www.eia.gov/electricity/data/eia923/. | [8 empty] | Check with fuel supplier or use U.S. Energy Information Administration (EIA) data for most recent year. Available at http://www.eia.gov/electricity/data/eia923/.
| Percent ash content for Coal (% weight) | 5.84 | Average ash content based on U.S. coal data for 2016 compiled by the U.S. Energy Information Administration (EIA) from data reported on EIA Form EIA-923, Power Plant Operations Report. Available at http://www.eia.gov/electricity/data/eia923/. | [8 empty] | Check with fuel supplier or use U.S. Energy Information Administration (EIA) data for most recent year. Available at http://www.eia.gov/electricity/data/eia923/.
| Higher Heating Value (HHV) (Btu/lb) | 8826 | 2016 coal data compiled by the Office of Oil, Gas, and Coal Supply Statistics, U.S. Energy Information Administration (EIA) from data reported on EIA Form EIA-923, Power Plant Operations Report. Available at http://www.eia.gov/electricity/data/eia923/. | [8 empty] | Fuel supplier or use U.S. Energy Information Administration (EIA) data for most recent year. Available at http://www.eia.gov/electricity/data/eia923/.
| Interest Rate | 3.25 | Default bank prime rate |  |  |  |  | Bank prime rate is as of March 2, 2021 and is available as the rates listed under 'bank prime loan' at https://www.federalreserve.gov/releases/h15/. |  |  |  | Use current bank prime rate available at https://www.federalreserve.gov/releases/h15/.
Reset Form
Calculate
Reset

## SNCR Design Parameters
SNCR Design Parameters
The following design parameters for the SNCR were calculated based on the values entered on the Data Inputs tab. These values were used to prepare the costs shown on the Cost Estimate tab.
Parameter | Equation | Calculated Value | Units
Maximum Annual Heat Input Rate (QB) = | Bmw x NPHR = | 5580 | MMBtu/hour
Maximum Annual MWh Output = | Bmw x 8760 = | 4888080 | MWh
Estimated Actual Annual MWh Output (Boutput) = |  | 2797891.9233 | MWh
Heat Rate Factor (HRF) = | NPHR/10 = | 1
Total System Capacity Factor (CFtotal) = | (Boutput/Bmw)*(tsncr/tplant) = | 0.57239 | fraction
Total operating time for the SNCR (top) = | CFtotal x 8760 = | 5014.1432 | hours
NOx Removal Efficiency (EF) = | (NOxin - NOxout)/NOxin = | 3.2258 | percent
NOx removed per hour = | NOxin x EF x QB = | 33.48 | lb/hour
Total NOx removed per year = | (NOxin x EF x QB x top)/2000 = | 83.9368 | tons/year
Coal Factor (CoalF) = | 1 for bituminous; 1.05 for sub-bituminous; 1.07 for lignite (weighted average is used for coal blends) | 1.05 |  |  |  |  | #DIV/0!
SO2 Emission rate = | (%S/100)x(64/32)*(1x106)/HHV = | < 3 | lbs/MMBtu
Elevation Factor (ELEVF) = | 14.7 psia/P = |  |  | Not applicable; elevation factor does not apply to plants located at elevations below 500 feet.
Atmospheric pressure at 250 feet above sea level (P) = | 2116x[(59-(0.00356xh)+459.7)/518.6]5.256 x (1/144)* = | 14.5772 | psia
Retrofit Factor (RF) = | Retrofit to existing boiler | 1
* Equation is from the National Aeronautics and Space Administration (NASA), Earth Atmosphere Model. Available at https://spaceflightsystems.grc.nasa.gov/education/rocket/atmos.html.
Reagent Data:
Type of reagent used | Ammonia | Molecular Weight of Reagent (MW) = |  |  | 17.03 | g/mole | 1 | 56
|  |  |  | Density = | 56 | lb/gallon
Parameter | Equation | Calculated Value | Units
Reagent consumption rate (mreagent) = | (NOxin x QB x NSR x MWR)/(MWNOx x SR) = | 403.3656 | lb/hour
(whre SR = 1 for NH3; 2 for Urea)
Reagent Usage Rate (msol) = | mreagent/Csol = | 1390.9159 | lb/hour
| (msol x 7.4805)/Reagent Density = | 185.799 | gal/hour
Estimated tank volume for reagent storage = | (msol x 7.4805 x tstorage x 24 hours/day)/Reagent Density = | 62500 | gallons (storage needed to store a 14 day reagent supply rounded up to the nearest 100 gallons)
Capital Recovery Factor:
Parameter | Equation | Calculated Value
Capital Recovery Factor (CRF) = | i (1+ i)n/(1+ i)n - 1 = | 0.0944
Where n = Equipment Life and i= Interest Rate
Parameter | Equation | Calculated Value | Units
Electricity Usage:
Electricity Consumption (P) = | (0.47 x NOxin x NSR x QB)/NPHR = | 51.2194 | kW/hour
Water Usage:
Water consumption (qw) = | (msol/Density of water) x ((Cstored/Cinj) - 1) = | 316.6855 | gallons/hour
Fuel Data:
Additional Fuel required to evaporate water in injected reagent (ΔFuel) = | Hv x mreagent x ((1/Cinj)-1) = | 3.2673 | MMBtu/hour
Ash Disposal:
Additional ash produced due to increased fuel consumption (Δash) = | (Δfuel x %Ash x 1x106)/HHV = | 21.6189 | lb/hour

## Cost Estimate
Cost Estimate
Total Capital Investment (TCI)
For Coal-Fired Boilers:
TCI = 1.3 x (SNCRcost + APHcost + BOPcost)
For Fuel Oil and Natural Gas-Fired Boilers:
TCI = 1.3 x (SNCRcost + BOPcost)
Capital costs for the SNCR (SNCRcost) = | 3689655.2603 | in 2019 dollars
Air Pre-Heater Costs (APHcost)* = | 0 | in 2019 dollars
Balance of Plant Costs (BOPcost) = | 4408602.7231 | in 2019 dollars
Total Capital Investment (TCI) = | 10527735.3784 | in 2019 dollars
* Not applicable - This factor applies only to coal-fired boilers that burn bituminous coal and emits equal to or greater than 0.3lb/MMBtu of sulfur dioxide.
SNCR Capital Costs (SNCRcost)
For Coal-Fired Utility Boilers:
SNCRcost = 220,000 x (BMW x HRF)0.42 x CoalF x BTF x ELEVF x RF
For Fuel Oil and Natural Gas-Fired Utility Boilers:
SNCRcost = 147,000 x (BMW x HRF)0.42 x ELEVF x RF
For Coal-Fired Industrial Boilers:
SNCRcost = 220,000 x (0.1 x QB x HRF)0.42 x CoalF x BTF x ELEVF x RF
For Fuel Oil and Natural Gas-Fired Industrial Boilers:
SNCRcost = 147,000 x ((QB/NPHR)x HRF)0.42 x ELEVF x RF
SNCR Capital Costs (SNCRcost) = | 3689655.2603 | in 2019 dollars |  | ELEVF | 1
Air Pre-Heater Costs (APHcost)*
For Coal-Fired Utility Boilers:
APHcost = 69,000 x (BMW x HRF x CoalF)0.78 x AHF x RF
For Coal-Fired Industrial Boilers:
APHcost = 69,000 x (0.1 x QB x HRF x CoalF)0.78 x AHF x RF
Air Pre-Heater Costs (APHcost) = | 0 | in 2019 dollars
* Not applicable - This factor applies only to coal-fired boilers that burn bituminous coal and emit equal to or greater than 3lb/MMBtu of sulfur dioxide.
Balance of Plant Costs (BOPcost)
For Coal-Fired Utility Boilers:
BOPcost = 320,000 x (BMW)0.33 x (NOxRemoved/hr)0.12 x BTF x RF
For Fuel Oil and Natural Gas-Fired Utility Boilers:
BOPcost = 213,000 x (BMW)0.33 x (NOxRemoved/hr)0.12 x RF
For Coal-Fired Industrial Boilers:
BOPcost = 320,000 x (0.1 x QB)0.33 x (NOxRemoved/hr)0.12 x BTF x RF
For Fuel Oil and Natural Gas-Fired Industrial Boilers:
BOPcost = 213,000 x (QB/NPHR)0.33 x (NOxRemoved/hr)0.12 x RF
Balance of Plant Costs (BOPcost) = | 4408602.7231 | in 2019 dollars |  |  | 1 | BTF
320000
558
Annual Costs
Total Annual Cost (TAC)
TAC = Direct Annual Costs + Indirect Annual Costs
Direct Annual Costs (DAC) = | 480382.3007 | in 2019 dollars
Indirect Annual Costs (IDAC) = | 998555.7006 | in 2019 dollars
Total annual costs (TAC) = DAC + IDAC | 1478938.0013 | in 2019 dollars
Direct Annual Costs (DAC)
DAC = (Annual Maintenance Cost) + (Annual Reagent Cost) + (Annual Electricity Cost) + (Annual Water Cost) + (Annual Fuel Cost) + (Annual Ash Cost)
Annual Maintenance Cost = | 0.015 x TCI = | 157916.0307 | in 2019 dollars
Annual Reagent Cost = | qsol x Costreag x top = | 272965.5346 | in 2019 dollars
Annual Electricity Cost = | P x Costelect x top = | 9271.2488 | in 2019 dollars
Annual Water Cost = | qwater x Costwater x top = | 6621.569 | in 2019 dollars
Additional Fuel Cost = | ΔFuel x Costfuel x top = | 30962.956 | in 2019 dollars
Additional Ash Cost = | ΔAsh x Costash x top x (1/2000) = | 2644.9615 | in 2019 dollars
Direct Annual Cost = |  | 480382.3007 | in 2019 dollars
Indirect Annual Cost (IDAC)
IDAC = Administrative Charges + Capital Recovery Costs
Administrative Charges (AC) = | 0.03 x Annual Maintenance Cost = | 4737.4809 | in 2019 dollars
Capital Recovery Costs (CR)= | CRF x TCI = | 993818.2197 | in 2019 dollars
Indirect Annual Cost (IDAC) = | AC + CR = | 998555.7006 | in 2019 dollars
Cost Effectiveness
Cost Effectiveness = Total Annual Cost/ NOx Removed/year
Total Annual Cost (TAC) = | 1478938.0013 | per year in 2019 dollars
NOx Removed = | 83.9368 | tons/year
Cost Effectiveness = | 17619.6704 | per ton of NOx removed in 2019 dollars