## Cover Page
Appendix G-7
Updated in Response to Comments
FutureFuel Cost Calculations
Division of Environmental Quality
Office of Air Quality

## FFCC Read Me
Annual Baseline Emissions
| SO2 | Nox | Data Source
2017 | 2139 | 241 | EIS Gateway
2018 | 2319 | 268 | EIS Gateway
2019 | 2055 | 231 | DEQ EI Submission
Avg | 2171 | 246.6667
At DEQ's request , FutureFuel provided emission reduction and cost-effectiveness based on the maximum monthly emission rate during the baseline period. After consultation with EPA and other states, DEQ is instead calculating emission reductions and cost-effectiveness based on annual average emission rates for the three coil-fired boilers .
DEQ made the following additional revisions for consistency with the EPA control cost manual and similar technology assessments made during Regional Haze Planning Period 1.
  1)
  The EPA Control Cost Manual suggests use of 20% of total capital investment for contingency for study level cost estimates and 5 – 15% for “mature control technologies.” Future fuel used 30% of capital costs (excluding energy and non-environmental capital costs that are part of total capital investment) in their cost calculations without providing an explanation of why this change was appropriate due to site-specific considerations.
Control Cost Manual Chapter 2, Page 30.
  2)
  AFUDC and Owner's costs, which are not valid costs under the EPA Control Cost Manual overnight estimation methodology have been removed. EPA has noted this in several actions on Planning Period I SIPs and FIPs.
  Control Cost Manual Chapter 2, Page 11 and 17
  3)
  All line-item costs estimated using total capital investment were revised to reflect changes in contingency and removal of disallowed costs using formulas provided by the EPA control cost manual
  Administrative costs = 2% of capital investment
  Property tax =1 % of capital investment
  Insurance = 1% of capital investment
  Control Cost Manual Chapter 2, Page 35
  4)
  Equipment Life for control technologies has been revised to be consistent with EPA control cost manual and similar technology assessments made during Regional Haze Planning Period 1.
Wet FGD: 30 years
Dry FGD: 30 years
DSI: 30 years
SCR: 30 years
SNCR: 20 years
  5)
  Cost of fuel for natural gas scenarios revised to reflect the incremental change in cost of using natural gas compared to coals currently in use for boilers based on EIA data. In addition, the cost associated with electrical, maintenance, operating and support labor, permitting and compliance were removed because these do not represent cost increases above the current cost of using coal. See Email from Philip Antici on July 23, 2020.
  6)
  Costs for each lower sulfur content coal scenario were revised to reflect the incremental cost of the scenario above current costs for coal. The tax associated with the 1.5% sulfur content coal control scenario was adjusted to remove cost of transportation from the taxable amount. In addition, the control efficiency was adjusted to reflect emission reductions resulting from switching coals without making changes to emissions from waste streams in the baseline. This change reflects a mass-balance estimation of SO2 emitted from burning coal and the average sulfur content of the coals burned during the baseline instead of the permitted sulfur content limit for coal. (See email from Philip Antici on 7/23/ 20 and FFCC Coal and Waste SO2 mmBtu Baseline_9_8_2020 spreadsheet.
In response to public comments, cost calculations were modified to correct identified errors. See Response to Comments for discussion of the rationale for these changes.

## FFCC Boiler replacement x 3
Incremental Fuel Cost Calculations
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 11191485 |  |  | Coal-Fired Boilers
20% Contingency (0.2*Direct and Indirect Capital Investment) | 2238297 |  |  | 150000 | lb steam | 1 | btu | 1 | lb coal | 1 | short ton | 43.5 | $ | Northern Appalachia (<3% SO2, 13000lb/btu, EIA accessed on 7/17/20)
Total Capital Investment (TCI) | 13429782 |  |  | 1 | hr | 970 | lb steam | 11100 | btu | 2000 | lb | 1 | short ton
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I = 0.07), n = 30 years |  | 0.00030301
Natural Gas Fired Boilers
Annualized Capital Investment | 1082257.8313 |  |  | 150000 | lb steam | 1 | btu | 1 | MMbtu | 1.7 | $ | Midwest Region Natural Gas (EIA accessed on 7/17/20)
Annual Operating and Maintenance Costs |  |  |  | 1 | hr | 970 | lb steam | 1000000 | btu | 1 | Mmbtu
Fuel | -623677.2019 | See incremental fuel cost calculations |  | 0.00026289
Incremental Electrical Costs | 0
Incremental Maintenance Costs | 0
Incremental Operating And Support Labor Costs | 0
Incremental Permitting and Compliance Costs | 0 |  |  | -13.24%
Offsite Liquid Waste Disposal Costs | 25047907.5631
Offsite Dewatered Sludge Disposal Costs | 205086 |  |  | It is 13% cheaper to operate using natural gas, this does not account for the cost of transportation of coal. FutureFuels already has existing pipeline infrastructure for its other natural gas units therefore there should not be additional cost associated with transport of gas).
Offsite Disposal Support Labor Costs | 129632
Total Annual Operating and Maintenance Costs | 24758948.3611 |  |  | % change (%) = (cost of natural gas to generate 1 lb of steam (N) minus cost of coal to generate 1 lb steam(C))/(cost of coal to generate 1 lb of steam(C))
Indirect Annual Costs
Overhead | 77779.2 |  |  | %=(N-C)/C | C%=N-C | C+C% = N | C(1+%)=N | C=N/(1+%)
Administrative | 268595.64
Property Tax | 134297.82 |  |  | N= | 4086385
Insurance | 134297.82
Total Indirect Annual Cost | 614970.48 |  |  | C= | 4710062.2019
Total Annual Cost | 26456176.6725
-623677.2019
| SO2 | NOx | Both
Average Annual Baseline Emissions (tons) | 2171 | 246.6667 |  |  | 623,677 cheaper to burn natural gas per year than current fuel
Control Efficiency | 99% | 90%
Estimated Emission Reductions (tons) | 2149.29 | 222 | 2371.29
Cost-Effectiveness ($/ton) | 12309.2634 | 119171.967 | 11156.871

## FFCC Boiler retrofit to gas x 3
Incremental Fuel Cost Calculations
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 10646285 |  |  | Coal-Fired Boilers
20% Contingency (0.2*Direct and Indirect Capital Investment) | 2129257 |  |  | 150000 | lb steam | 1 | btu | 1 | lb coal | 1 | short ton | 43.5 | $ | Northern Appalachia (<3% SO2, 13000lb/btu, EIA accessed on 7/17/20)
Total Capital Investment (TCI) | 12775542 |  |  | 1 | hr | 970 | lb steam | 11100 | btu | 2000 | lb | 1 | short ton
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I = 0.07, n = 30 years |  | 0.00030301
Natural Gas Fired Boilers
Annualized Capital Investment | 1029534.9827 |  |  | 150000 | lb steam | 1 | btu | 1 | MMbtu | 1.7 | $ | Midwest Region Natural Gas (EIA accessed on 7/17/20)
Annual Operating and Maintenance Costs |  |  |  | 1 | hr | 970 | lb steam | 1000000 | btu | 1 | Mmbtu
Fuel | -623677.2019 | See incremental fuel cost calculations |  | 0.00026289
Incremental Electrical Costs | 0
Incremental Maintenance Costs | 0
Incremental Operating And Support Labor Costs | 0
Incremental Permitting and Compliance Costs | 0 |  |  | -13.24%
Offsite Liquid Waste Disposal Costs | 25047907.5631
Offsite Dewatered Sludge Disposal Costs | 205086 |  |  | It is 13% cheaper to operate using natural gas, this does not account for the cost of transportation of coal. FutureFuels already has existing pipeline infrastructure for its other natural gas units therefore there should not be additional cost associated with transport of gas).
Offsite Disposal Support Labor Costs | 129632
Total Annual Operating and Maintenance Costs | 24758948.3611 |  |  | % change (%) = (cost of natural gas to generate 1 lb of steam (N) minus cost of coal to generate 1 lb steam(C))/(cost of coal to generate 1 lb of steam(C))
Indirect Annual Costs
Overhead | 77779.2 |  |  | %=(N-C)/C | C%=N-C | C+C% = N | C(1+%)=N | C=N/(1+%)
Administrative | 255510.84
Property Tax | 127755.42 |  |  | N= | 4086385
Insurance | 127755.42
Total Indirect Annual Cost | 588800.88 |  |  | C= | 4710062.2019
Total Annual Cost | 26377284.2238
-623677.2019
| SO2 | NOx | Both
Average Annual Baseline Emissions (tons) | 2171 | 246.6667 |  |  | 623,677 cheaper to burn natural gas per year than current fuel
Control Efficiency | 99% | 90%
Estimated Emission Reductions (tons) | 2149.29 | 222 | 2371.29
Cost-Effectiveness ($/ton) | 12272.5571 | 118816.5956 | 11123.6012

## FFCC Boiler replacement x 1
Incremental Fuel Cost Calculations
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 7033162 |  |  | Coal-Fired Boilers
20% Contingency (0.2*Direct and Indirect Capital Investment) | 1406632.4 |  |  | 150000 | lb steam | 1 | btu | 1 | lb coal | 1 | short ton | 43.5 | $ | Northern Appalachia (<3% SO2, 13000lb/btu, EIA accessed on 7/17/20)
Total Capital Investment (TCI) | 8439794.4 |  |  | 1 | hr | 970 | lb steam | 11100 | btu | 2000 | lb | 1 | short ton
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I = 0.07, n = 30 years |  | 0.00030301
Natural Gas Fired Boilers
Annualized Capital Investment | 680132.6771 |  |  | 150000 | lb steam | 1 | btu | 1 | MMbtu | 1.7 | $ | Midwest Region Natural Gas (EIA accessed on 7/17/20)
Annual Operating and Maintenance Costs |  |  |  | 1 | hr | 970 | lb steam | 1000000 | btu | 1 | Mmbtu
Fuel | -292507.2687 | See incremental fuel cost calculations |  | 0.00026289
Incremental Electrical Costs | 0
Incremental Maintenance Costs | 0
Incremental Operating And Support Labor Costs | 0
Incremental Permitting and Compliance Costs | 0 |  |  | -13.24%
Offsite Liquid Waste Disposal Costs | 8465663
Offsite Dewatered Sludge Disposal Costs | 68363 |  |  | It is 13% cheaper to operate using natural gas, this does not account for the cost of transportation of coal. FutureFuels already has existing pipeline infrastructure for its other natural gas units therefore there should not be additional cost associated with transport of gas).
Offsite Disposal Support Labor Costs | 25926
Total Annual Operating and Maintenance Costs | 8267444.7313 |  |  | % change (%) = (cost of natural gas to generate 1 lb of steam (N) minus cost of coal to generate 1 lb steam(C))/(cost of coal to generate 1 lb of steam(C))
Indirect Annual Costs
Overhead | 15555.6 |  |  | %=(N-C)/C | C%=N-C | C+C% = N | C(1+%)=N | C=N/(1+%)
Administrative | 168795.888
Property Tax | 84397.944 |  |  | N= | 1916532
Insurance | 84397.944
Total Indirect Annual Cost | 353147.376 |  |  | C= | 2209039.2687
Total Annual Cost | 9300724.7844
-292507.2687
| SO2 | NOx | Both
Average Annual Baseline Emissions (tons) | 2171 | 246.6667
Average Annual Baseline Coal Only (tons) | 2091.6804
Control Efficiency | 33% | 30%
Estimated Emission Reductions (tons) | 690.2545 | 74 | 764.2545
Effective Control Efficiency | 31.79%
Cost-Effectiveness ($/ton) | 13474.3407 | 125685.4701 | 12169.669

## FFCC Boiler retrofit to gas x1
Incremental Fuel Cost Calculations
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 5509762 |  |  | Coal-Fired Boilers
20% Contingency (0.2*Direct and Indirect Capital Investment) | 1101952.4 |  |  | 150000 | lb steam | 1 | btu | 1 | lb coal | 1 | short ton | 43.5 | $ | Northern Appalachia (<3% SO2, 13000lb/btu, EIA accessed on 7/17/20)
Total Capital Investment (TCI) | 6611714.4 |  |  | 1 | hr | 970 | lb steam | 11100 | btu | 2000 | lb | 1 | short ton
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I =7%, n = 30 years |  | 0.00030301
Natural Gas Fired Boilers
Annualized Capital Investment | 532814.2845 |  |  | 150000 | lb steam | 1 | btu | 1 | MMbtu | 1.7 | $ | Midwest Region Natural Gas (EIA accessed on 7/17/20)
Annual Operating and Maintenance Costs |  |  |  | 1 | hr | 970 | lb steam | 1000000 | btu | 1 | Mmbtu
Fuel | -292507.2687 | See incremental fuel cost calculations |  | 0.00026289
Incremental Electrical Costs | 0
Incremental Maintenance Costs | 0
Incremental Operating And Support Labor Costs | 0
Incremental Permitting and Compliance Costs | 0 |  |  | -13.24%
Offsite Liquid Waste Disposal Costs | 8465663
Offsite Dewatered Sludge Disposal Costs | 68363 |  |  | It is 13% cheaper to operate using natural gas, this does not account for the cost of transportation of coal. FutureFuels already has existing pipeline infrastructure for its other natural gas units therefore there should not be additional cost associated with transport of gas).
Offsite Disposal Support Labor Costs | 25926
Total Annual Operating and Maintenance Costs | 8267444.7313 |  |  | % change (%) = (cost of natural gas to generate 1 lb of steam (N) minus cost of coal to generate 1 lb steam(C))/(cost of coal to generate 1 lb of steam(C))
Indirect Annual Costs
Overhead | 15555.6 |  |  | %=(N-C)/C | C%=N-C | C+C% = N | C(1+%)=N | C=N/(1+%)
Administrative | 132234.288
Property Tax | 66117.144 |  |  | N= | 1916532
Insurance | 66117.144
Total Indirect Annual Cost | 280024.176 |  |  | C= | 2209039.2687
Total Annual Cost | 9080283.1919
-292507.2687
| SO2 | NOx | Both
Average Annual Baseline Emissions (tons) | 2171 | 246.6667
Average Annual Baseline Emissions for Coal Only (tons) | 2091.6804
Control Efficiency | 33% | 30%
Estimated Emission Reductions (tons) | 690.2545 | 74 | 764.2545
Effective Control Efficiency | 31.79%
Cost-Effectiveness ($/ton) | 13154.9779 | 122706.5296 | 11881.229

## FFC LSC
Costs for each lower sulfur content coal scenario were revised to reflect the incremental cost of the scenario above current costs for coal. The tax associated with the 1.5% sulfur content coal control scenario was adjusted to remove cost of transportation from the taxable amount. In addition, the control efficiency was adjusted to reflect emission reductions resulting from switching coals without making changes to emissions from waste streams in the baseline. This change reflects a mass-balance estimation of SO2 emitted from burning coal and the average sulfur content of the coals burned during the baseline instead of the permitted sulfur content limit for coal. (See email from Philip Antici on 7/23/ 20 and FFCC Coal and Waste SO2 mmBtu Baseline_9_8_2020 spreadsheet.
2017 - 2019 FFCC Baseline Coal Data
|  | Sulfur Content Control Scenarios |  |  | CFBs Year | BLR 1 mmBtu/yr | BLR 2 mmBtu/yr | BLR 3 mmBtu/yr | All Coal-Fired Boilers mmBtu/yr | ton SO2/yr
|  | 2.5% | 2% | 1.5%
| Incremental Increase in Cost ($) | 684000 | 1187500 | 2519500 | 2017 | 310960.9378 | 311682.2481 | 262666.4642 | 885309.6501 | 2061.8086
| Tax ($) | 54720 | 95000 | 160000 | 2018 | 254561.7221 | 274153.9334 | 221517.3534 | 750233.0089 | 2269.6526
| Total Annual Cost ($ 2019) | 738720 | 1282500 | 2679500 | 2019 | 245435.6 | 298760.9043 | 282516.5909 | 826713.0952 | 1943.5801
| Average Annual Baseline Emissions (all fuels tons) | 2171 | 2171 | 2171
| Average Annual Baseline Emissions (coal only tons) | 2091.6804 | 2091.6804 | 2091.6804
| Percent Reduction in Coal Sulfur Content | 10.3% | 28.24% | 46.18% | Total Heat Input
| Estimated Emission Reductions (tons) | 215.3973 | 590.6539 | 965.9105 | All Feed Year | CFBs mmBtu/yr | Waste mmBtu/yr | Total mmBtu/yr
| Effective Control Efficiency(%) | 9.922% | 27.21% | 44.49%
| Cost-Effectiveness ($/ton) | 3429.5694 | 2171.3222 | 2774.0664 | 2017 | 885309.6501 | 116684.5525 | 1001994.2026
| Incremental Cost-Effectiveness 2.5% | 0 | 1449.0883 | 2585.937 | 2018 | 750233.0089 | 138494.3628 | 888727.3717
| Incremental Cost-Effectiveness 2% | 0 | 0 | 3722.7857 | 2019 | 826713.0952 | 113378.5158 | 940091.611
Annual Baseline Emissions (All Fuels)
[6 empty] | SO2 | Nox | Data Source
[5 empty] | 2017 | 2139 | 241 | EIS Gateway
[5 empty] | 2018 | 2319 | 268 | EIS Gateway
[5 empty] | 2019 | 2055 | 231 | DEQ EI Submission
[5 empty] | Avg | 2171 | 246.6667

## FFCC Wet Scrubber
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 57853376 | AFUDC, Owner's Costs, Contingency subtracted from capital costs provided by FutureFuel
20% Contingency (0.2*Direct and Indirect Capital Investment) | 11570675.2
Total Capital Investment (TCI) | 69424051.2
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I =7%, n = 30 years
Annualized Capital Investment | 5594634.6034
Annual Operating and Maintenance Costs
Fixed Additional Operating Labor Costs | 2166649
Fixed AdditionalMaintenance Labor and Materials | 448041
Additional Administrative Labor Costs | 70376
Variable Sorbent Cost | 6742
Variable Cost Waste Disposal of Sorbent | 332983
Variable cost of Additional Power, Makeup Water, and Sulfuric Acid | 18424
Total Annual Operating and Maintenance Costs | 3043215
Indirect Annual Costs
Overhead | 1611039.6
Administrative | 1388481.024
Property Tax | 694240.512
Insurance | 694240.512
Total Indirect Annual Cost | 4388001.648
Total Annual Cost | 13025851.2514
SO2
Average Annual Baseline Emissions (tons) | 2171
Control Efficiency | 94%
Estimated Emission Reductions (tons) | 2040.74
Cost-Effectiveness ($/ton) | 6382.9058

## FFCC SDA
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 49722467 | AFUDC, Owner's Costs, Contingency subtractd from capital costs provided by FutureFuel
20% Contingency (0.2*Direct and Indirect Capital Investment) | 9944493.4
Total Capital Investment (TCI) | 59666960.4
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I =7%, n = 30 years
Annualized Capital Investment | 4808345.7471
Annual Operating and Maintenance Costs
Fixed Additional Operating Labor Costs | 1444433
Fixed Additional Maintenance Labor and Materials | 173063
Additional Administrative Labor Costs | 45410
Variable Sorbent Cost | 6763
Variable Cost Waste Disposal of Sorbent | 379506
Variable cost of Additional Power and Make Up Water | 18424
Total Annual Operating and Maintenance Costs | 2067599
Indirect Annual Costs
Overhead | 997743.6
Administrative | 1193339.208
Property Tax | 596669.604
Insurance | 596669.604
Total Indirect Annual Cost | 3384422.016
Total Annual Cost | 10260366.7631
SO2
Average Annual Baseline Emissions (tons) | 2171
Control Efficiency | 92%
Estimated Emission Reductions (tons) | 1997.32
Cost-Effectiveness ($/ton) | 5137.0671

## FFCC DSI
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 48992316 | Owner's Costs, Contingency subtracted from capital costs provided by FutureFuel
20% Contingency (0.2*Direct and Indirect Capital Investment) | 9798463.2
Total Capital Investment (TCI) | 58790779.2
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I =7%, n = 30 years
Annualized Capital Investment | 4737737.4553
Annual Operating and Maintenance Costs
Fixed Additional Operating Labor Costs | 361108
Fixed Additional Maintenance Labor and Materials | 112972
Additional Administrative Labor Costs | 12189
Variable Sorbent Cost | 18206
Variable Cost Waste Disposal of Sorbent | 397132
Variable cost of Additional Power | 19860
Total Annual Operating and Maintenance Costs | 921467
Indirect Annual Costs
Overhead | 291761.4
Administrative | 1175815.584
Property Tax | 587907.792
Insurance | 587907.792
Total Indirect Annual Cost | 2643392.568
Total Annual Cost | 8302597.0233
SO2
Average Annual Baseline Emissions (tons) | 2171
Control Efficiency | 40%
Estimated Emission Reductions (tons) | 868.4
Cost-Effectiveness ($/ton) | 9560.798

## FFCC SCR
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 38525286
20% Contingency (0.2*Direct and Indirect Capital Investment) | 7705057.2
Total Capital Investment (TCI) | 46230343.2
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I =7%, n = 30 years
Annualized Capital Investment | 3725537.0916
Annual Operating and Maintenance Costs
Maintenance | 239320
Reagent | 216051
Electricity | 66018
Catalyst Replacement | 19664
Total Annual Operating and Maintenance Costs | 541053
Indirect Annual Costs
Overhead | 143592
Administrative | 924606.864
Property Tax | 462303.432
Insurance | 462303.432
Total Indirect Annual Cost | 1992805.728
Total Annual Cost | 6259395.8196
NOx
Average Annual Baseline Emissions (tons) | 246.6667
Control Efficiency | 80%
Estimated Emission Reductions (tons) | 197.3333
Cost-Effectiveness ($/ton) | 31719.9112

## FFCC SNCR
Capital Investment | Estimate | Notes
Direct and Indirect Capital Investment | 21400466
20% Contingency (0.2*Direct and Indirect Capital Investment) | 4280093.2
Total Capital Investment (TCI) | 25680559.2
CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.080586 | I =7%, n = 30 years
Annualized Capital Investment | 2069503.9061
Annual Operating and Maintenance Costs
Maintenance | 219462
Reagent | 189948
Electricity | 2845
Water, Additional Fuel, Additional Ash Cost | 1440
Total Annual Operating and Maintenance Costs | 413695
Indirect Annual Costs
Administrative | 6583.86
Total Indirect Annual Cost | 6583.86
Total Annual Cost | 2489782.7661
NOx
Average Annual Baseline Emissions (tons) | 246.6667
Control Efficiency | 40%
Estimated Emission Reductions (tons) | 98.6667
Cost-Effectiveness ($/ton) | 25234.2848

## CEPCI Index
Year (n) | CEPCI Index Value | Cost Index Ratio (Value2019/Valuen)
1998 | 389.5 | 1.5597
1999 | 390.6 | 1.5553
2000 | 394.1 | 1.5415
2001 | 394.3 | 1.5407
2002 | 395.6 | 1.5356
2003 | 402 | 1.5112
2004 | 444.2 | 1.3676
2005 | 468.2 | 1.2975
2006 | 499.6 | 1.216
2007 | 525.4 | 1.1563
2008 | 575.4 | 1.0558
2009 | 521.9 | 1.164
2010 | 550.8 | 1.1029
2011 | 585.7 | 1.0372
2012 | 584.6 | 1.0392
2013 | 567.2 | 1.0711
2014 | 576.1 | 1.0545
2015 | 556.8 | 1.0911
2016 | 541.7 | 1.1215
2017 | 567.5 | 1.0705
2018 | 603.1 | 1.0073
2019 | 607.5 | 1

## Offsite Waste Costs 2022
Waste | Cost/lb | Comment | 2022 Increase | Year | Amount Burned in Boiler | Year | Original | 2022 Update
High Btu Waste | 0.22 | Vendor Quote 3/12/20 | 0.253 | 2021 | 14144276 | 2020 | 14693750 | 17819058
Solvent Waste (Boiler Waste) | 0.52 | Vendor Quote 3/12/20 | 0.598 | 2020 | 17872279 | 2021 | 15140674.4829 | 18175439.16
Low BTU Waste | 0.31 | Vendor Quote 3/12/20 | 0.3565 | 2019 | 21892563 | 2022 | 15601192.602 | 18538947.9432
Low BTU Acidic Waste | 0.52 | Vendor Quote 3/12/20 | 0.598 | 2018 | 26487615 | 2023 | 16075717.821 | 18909726.9021
|  |  |  | 2017 | 20614276 | 2024 | 16564676.179 | 19287921.4401
|  |  |  | 2016 | 25758983 | 2025 | 17068506.674 | 19673679.8689
|  |  |  | 2015 | 24554338 | 2026 | 17587661.6561 | 20067153.4663
|  |  |  | 2014 | 30757480 | 2027 | 18122607.2343 | 20468496.5356
32,317,116 lb x $0.50/lb (Disposal Estimate) = $16,158,558 |  |  |  | 2013 | 31887107 | 2028 | 18673823.6948 | 20877866.4663
At least 750 shipments x $2,214/shipment = $1,660,500 |  |  |  | 2012 | 30878782 | 2029 | 19241805.932 | 21295423.7956
How to quantify cost of resources to ship twice per day? |  |  |  | 2011 | 32776271 | 2030 | 19827063.8931 | 21721332.2716
Estimating $17,819,058 annual or $342,674 per week. | [5 empty] | 2031 | 20430123.0357 | 22155758.917
|  |  |  | Max Yr | 32776271 | 2032 | 21051524.7999 | 22598874.0953
|  |  |  | Max Mo | 2693093 | 2033 | 21691827.0941 | 23050851.5772
Waste combustion amounts are direcly proportional to FFCC's business. FFCC business tends to be cyclical and FFCC expects business to return to higher levels as seen in 2010 to 2014 levels. The years of 2020 - 2022 are abnormal and has been impacted by a pandemic, oversea wars, supply chain disruptions, and other unusual circumstances beyond FFCC's control. |  |  |  | Annualized | 32317116 | 2034 | 22351604.7959 | 23511868.6088
[6 empty] | 2035 | 23031450.2686 | 23982105.981
[6 empty] | 2036 | 23731973.8927 | 24461748.1006
[6 empty] | 2037 | 24453804.6138 | 24950983.0626
|  |  |  | Year | DEQ Inflation Factor | 2038 | 25197590.5079 | 25450002.7238
|  |  |  | 2011 | 0.0135 | 2039 | 25963999.3625 | 25959002.7783
|  |  |  | 2012 | 0.0263 | 2040 | 26753719.2766 | 26478182.8339
|  |  |  | 2013 | 0.0177 | 2041 | 27567459.2785 | 27007746.4906
|  |  |  | 2014 | 0.015 | 2042 | 28405949.9621 | 27547901.4204
2020 was the base year for offsite disposal. The original offsite cost was inflated using a 3% annual increase. This is consistent with historical vendor increases. The DEQ price inflator (Implicit Price Deflator for the U.S. Gross National Product) is currently 5.8%, but the 10-year average is 2% and climbing (see adjacent table). FFCC will use the 2% factor for the 2022 Update. |  |  |  | 2015 | 0.0146 | 2043 | 29269944.1431 | 28098859.4488
|  |  |  | 2016 | 0.01 | 2044 | 30160217.5348 | 28660836.6378
|  |  |  | 2017 | 0.013 | 2045 | 31077569.4446 | 29234053.3705
|  |  |  | 2018 | 0.018 | 2046 | 32022823.4916 | 29818734.4379
|  |  |  | 2019 | 0.022 | 2047 | 32996828.3459 | 30415109.1267
|  |  |  | 2020 | 0.016 | 2048 | 34000458.491 | 31023411.3092
|  |  |  | 2021 | 0.013 | 2049 | 35034615.0085 | 31643879.5354
|  |  |  | 2022 | 0.058 | 2050 | 36100226.3871 | 32276757.1261
|  |  |  | 10yr Avg | 0.019758 | Avg 20 & 50 | 25396988.1936 | 25047907.5631
|  |  |  | 5Yr Avg | 0.0254
|  |  |  | 2yr Avg | 0.0355
Note on M2: Floyd, Thomas: Base year for offsite disposal. The original offsite cost was inflated using a factor 3% annual increase. This is consistent with historical vendor increases.
Note on N2: Floyd, Thomas: Base year for offsite disposal. The original offsite cost was inflated using a factor 3% annual increase. This is consistent with historical vendor increases. However, the average inflation over the past 10 years, using the DEQ price inflator, is currently 2% and climbing. FFCC will use the 2% factor for the 2022 Update.
Note on A10: TL Floyd: Waste that is burned in boilers is a mix of High Btu and Solvent Waste. So I averaged those two quotes to get $0.43/lb for boiler waste. then there is 16.5% envrionmental/fuel fee making it $0.50/lb Transportation quoted by the vendor in 2020 was $1925 per load. Diesel has more than doubled, but I will increase just 15%, making it now $2214 per load. Legacy charges just over $1,500 per load, but they can't handle this volume. The amount of waste is based on the worst month 2017 - 2019 and then annualizing it, which is 32,317,116 lbs/yr
Note on H14: a850836: Maximum amount burend in one year over the last 10-years.
Note on H15: a850836: Maximum amoung of waste burned in one month between 2018 and 2019. Did not have 2017 per month.
Note on H16: a850836: The maximum month in 2018-2019 was annualized to get the worst case year. This is very realistic since we actually combusted more in 2011.