## Cover Page
Appendix F-5
Entergy Cost Calculations
Division of Environmental Quality
Office of Air Quality

## Entergy Read Me
DRAFT
Read Me
In their response to DEQ’s ICR, Entergy calculated the cost of the compliance based on the assumption that the Independence units will cease coal-fired operations by December 31, 2030.
In addition, Entergy used a seven percent interest rate for annualizing capital costs. This interest rate is consistent with past cost analyses for regional haze planning and the social cost of rulemaking specified in the EPA Control Cost Manual. However, EPA Region 6 has indicated that DEQ should evaluate costs annualized based on the bank prime rate consistent with EPA Control Cost Manual guidance on private investments. The EPA Control Cost Manual recommends that assessments of private cost “should be prepared using firm-specific nominal interest rates if possible, or the bank prime rate if firm-specific interest rates cannot be estimated or verified.” Therefore, DEQ has calculated the annualized capital costs using the total capital investment estimates provided by Entergy and a 3.25% interest rate (bank prime rate on July 16, 2020).
For comparison, DEQ has also calculated annual costs based on the expected life of the control equipment evaluated in the event that these units were to continue to operate with no assumed operation cessation date. (See EAI Equipment Life Assumptions tab.) To evaluate the sensitivity of remaining useful life of Independence, DEQ also identified the year after which each strategy (averaged across both units) that is cost-effective based on equipment life would no longer be cost-effective. (See RUL Sensitivity tab.)
For Independence, costs were evaluated based on an average of both units because the units perform an identical function and have the same design. If only one unit were to install controls or cease operation, the other unit could run instead. Therefore, the estimated emission reductions of the control strategy would not be achieved.

## EAI RUL Assumptions
2030 Closure Assumed
Emission Unit | SO2 Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | WFGD | 401.82 | 126.0389 | 36.55 | 163.7751 | 9104 | 17989.352
| DGFD | 377.69 | 118.47 | 9.36 | 128.7626 | 8684 | 14827.5698
| Enhanced DSI | 335.58 | 68.5265 | 29.16 | 98.3992 | 6792 | 14487.5174
| DSI | 175 | 35.7356 | 16.6 | 52.7174 | 2587 | 20377.8096
Unit 2 | WFGD | 401.82 | 126.0389 | 36.55 | 163.7751 | 9786 | 16735.649
| DGFD | 377.69 | 118.47 | 9.36 | 128.7626 | 9342 | 13783.1959
| Enhanced DSI | 335.58 | 68.5265 | 29.16 | 98.3992 | 7347 | 13393.1153
| DSI | 175 | 35.7356 | 16.6 | 52.7174 | 2914 | 18091.0753
Units 1 and 2 averaged | WFGD | [5 empty] | 17362.5005
| DGFD | [5 empty] | 14305.3829
| Enhanced DSI | [5 empty] | 13940.3164
| DSI | [5 empty] | 19234.4424
Emission Unit | NOx Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | SCR | 186.32 | 58.443 | 3.42 | 62.3143 | 2267 | 27487.5698
| SNCR | 8.75 | 2.7446 | 6.53 | 9.3423 | 690 | 13539.5312
Unit 2 | SCR | 186.32 | 58.443 | 3.42 | 62.3143 | 1961 | 31776.8081
| SNCR | 8.75 | 2.7446 | 6.53 | 9.3423 | 298 | 31349.9213
Unit 1 and 2 averaged | SCR | [5 empty] | 29632.1889
| SNCR | [5 empty] | 22444.7263
CRF (2030 closure)
Equipment | Life Expectancy |  | Life Expectancy Reference |  | RUL | 3.25%
WFGD | 30 | years | EPA FIP AR TSD |  | 3.42 | 0.31367 | Calculated based on formula below
DGFD | 30 | years | EPA FIP AR TSD |  | 3.42 | 0.31367 | Calculated based on formula below
Enhanced DSI | 30 | years | EPA FIP OK TX TSD |  | 5.42 | 0.2042 | Calculated based on formula below
DSI | 30 | years | EPA FIP OK TX TSD |  | 5.42 | 0.2042 | Calculated based on formula below
SCR | 30 | years | Equipment Life Expectancy from Control Cost Manual |  | 3.42 | 0.31367 | Calculated based on formula below
SNCR | 20 | years | Equipment Life Expectancy from Control Cost Manual |  | 3.42 | 0.31367 | Calculated based on formula below
FGD & NOx strategies
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.31367
| interest |  | 0.0325 |  | bank prime rate
| n (remaining useful life or RUL) |  | 3.42
DSI Strategies
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.2042
| interest |  | 0.0325 |  | bank prime rate
| n (remaining useful life or RUL) |  | 5.42

## EAI Equipment Life Assumptions
Equipment Life Sensitivity Calculations
Emission Unit | SO2 Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | WFGD | 401.82 | 21.1686 | 36.55 | 58.1397 | 9104 | 6386.1667
| DGFD | 377.69 | 19.8974 | 9.36 | 29.4708 | 8684 | 3393.6906
| Enhanced DSI | 335.58 | 17.6789 | 29.16 | 47.1807 | 6792 | 6946.5033
| DSI | 175 | 9.2193 | 16.6 | 26.0077 | 2587 | 10053.2156
Unit 2 | WFGD | 401.82 | 21.1686 | 36.55 | 58.1397 | 9786 | 5941.1058
| DGFD | 377.69 | 19.8974 | 9.36 | 29.4708 | 9342 | 3154.6573
| Enhanced DSI | 335.58 | 17.6789 | 29.16 | 47.1807 | 7347 | 6421.7572
| DSI | 175 | 9.2193 | 16.6 | 26.0077 | 2914 | 8925.0751
Unit 1 and 2 averaged | WFGD | [5 empty] | 6163.6362
| DGFD | [5 empty] | 3274.1739
| Enhanced DSI | [5 empty] | 6684.1303
| DSI | [5 empty] | 9489.1453
Emission Unit | NOx Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | SCR | 186.32 | 9.8157 | 3.42 | 13.3322 | 2267 | 5880.9969
| SNCR | 8.75 | 0.60182 | 6.53 | 7.1838 | 690 | 10411.3716
Unit 2 | SCR | 186.32 | 9.8157 | 3.42 | 13.3322 | 1961 | 6798.6844
| SNCR | 8.75 | 0.60182 | 6.53 | 7.1838 | 298 | 24106.8671
Unit 1 and 2 average | SCR | [5 empty] | 6339.8407
| SNCR | [5 empty] | 17259.1193
CRF
Equipment | Life Expectancy |  | Life Expectancy Reference |  | RUL | 3.25%
WFGD | 30 | years | EPA FIP AR TSD |  |  | 0.052682 | Calculated based on formula below
DGFD | 30 | years | EPA FIP AR TSD |  |  | 0.052682 | Calculated based on formula below
Enhanced DSI | 30 | years | EPA FIP OK TX TSD |  |  | 0.052682 | Calculated based on formula below
DSI | 30 | years | EPA FIP OK TX TSD |  |  | 0.052682 | Calculated based on formula below
SCR | 30 | years | Equipment Life Expectancy from Control Cost Manual |  |  | 0.052682 | Calculated based on formula below
SNCR | 20 | years | Equipment Life Expectancy from Control Cost Manual |  |  | 0.068779 | Calculated based on formula below
| FGD & SCR strategies | [5 empty] | SNCR
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.052682 |  |  |  | CRF = (i(1+i)^n)/(((1+i)^n)-1) | 0.068779
| interest |  | 0.0325 |  | bank prime rate |  | interest | 0.0325
| n (remaining useful life or RUL) |  | 30 |  |  |  | n (remaining useful life or RUL) | 20
DSI Strategies
| CRF = (i(1+i)^n)/(((1+i)^n)-1) |  | 0.052682
| interest |  | 0.0325 |  | bank prime rate
| n (remaining useful life or RUL) |  | 30

## EAI RUL Sensitivity
Remaining Useful Life Sensitivity Calculations
Emission Unit Type | 98th Percentile
EGU Boiler | 5086
Emission Unit | SO2 Reduction Options | Capital Cost ($MM) | 2018 Annualized Capital Costs | 2018 Annual O&M Costs ($MM/yr) | 2019 Total Annual Costs ($MM/yr) | Emission Reductions (Avg Month Basis) | Cost-effectiveness ($2019/ton)
Unit 1 | DGFD | 377.69 | 36.0842 | 9.36 | 45.7758 | 8684 | 5271.2765
Unit 2 | DGFD | 377.69 | 36.0842 | 9.36 | 45.7758 | 9342 | 4899.9962
Units 1 & 2 averaged | DGFD | [5 empty] | 5085.6364
Equipment | Life Expectancy |  | 3.25%
DGFD | 13 | years | 0.095539
SIP Submission | Estimated EPA Approval Date | Estimated Compliance Date | Cost-Effective if Operate On or After
2021-07-31 | 2022-07-31 | 2027-07-31 | 2040-07-31
2021 | 2022 | 2027 | 2040

## CEPCI Index
Year (n) | CEPCI Index Value | Cost Index Ratio (Value2019/Valuen)
1998 | 389.5 | 1.5597
1999 | 390.6 | 1.5553
2000 | 394.1 | 1.5415
2001 | 394.3 | 1.5407
2002 | 395.6 | 1.5356
2003 | 402 | 1.5112
2004 | 444.2 | 1.3676
2005 | 468.2 | 1.2975
2006 | 499.6 | 1.216
2007 | 525.4 | 1.1563
2008 | 575.4 | 1.0558
2009 | 521.9 | 1.164
2010 | 550.8 | 1.1029
2011 | 585.7 | 1.0372
2012 | 584.6 | 1.0392
2013 | 567.2 | 1.0711
2014 | 576.1 | 1.0545
2015 | 556.8 | 1.0911
2016 | 541.7 | 1.1215
2017 | 567.5 | 1.0705
2018 | 603.1 | 1.0073
2019 | 607.5 | 1