## Cover Page
Appendix I-3
SWEPCO Flint Creek Revised Calculations
Division of Environmental Quality
Office of Air Quality

## SWEPCO Read Me
DRAFT | Baseline Operations for Flint Creek (June 2018 - December 2019) obtained from AMPD on June 9, 2020
| State | Facility Name | Facility ID (ORISPL) | Unit ID | Associated Stacks | Month | Year | Program(s) | Operating Time | SO2 (tons) | Avg. NOx Rate (lb/MMBtu) | NOx (tons) | CO2 (short tons) | Heat Input (MMBtu) | # of hours in month
| AR | Flint Creek Power Plant | 6138 | 1 |  | 6 | 2018 | ARP, CSOSG2, MATS | 712.47 | 78.697 | 0.1903 | 289.889 | 310728.161 | 2962700.24 | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 7 | 2018 | ARP, CSOSG2, MATS | 704.06 | 80.933 | 0.1939 | 297.571 | 315030.08 | 3003730.352 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 8 | 2018 | ARP, CSOSG2, MATS | 744 | 81.942 | 0.1941 | 309.944 | 326744.1 | 3115403.1 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 9 | 2018 | ARP, CSOSG2, MATS | 675.2 | 76.412 | 0.1936 | 271.566 | 284854.88 | 2716007.36 | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 10 | 2018 | ARP, CSOSG2, MATS | 471.68 | 61.868 | 0.1892 | 197.989 | 208697.043 | 1989865.15 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 11 | 2018 | ARP, CSOSG2, MATS | 720 | 99.289 | 0.2003 | 338.715 | 353283.8 | 3368453.6 | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 12 | 2018 | ARP, CSOSG2, MATS | 744 | 101.808 | 0.1991 | 345.06 | 362414.7 | 3455512 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 1 | 2019 | ARP, CSOSG2, MATS | 744 | 101.249 | 0.188 | 327.439 | 362755.6 | 3458765.2 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 2 | 2019 | ARP, CSOSG2, MATS | 672 | 83.996 | 0.1887 | 282.317 | 310853.1 | 2963891.4 | 672
| AR | Flint Creek Power Plant | 6138 | 1 |  | 3 | 2019 | ARP, CSOSG2, MATS | 687.92 | 79.67 | 0.1851 | 245.663 | 278500.505 | 2655415.475 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 4 | 2019 | ARP, CSOSG2, MATS | 0 | [5 empty] | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 5 | 2019 | ARP, CSOSG2, MATS | 569.89 | 59.194 | 0.1854 | 206.232 | 224624.11 | 2141725.011 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 6 | 2019 | ARP, CSOSG2, MATS | 720 | 72.929 | 0.1813 | 227.277 | 261804.6 | 2496223.3 | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 7 | 2019 | ARP, CSOSG2, MATS | 744 | 80.204 | 0.1809 | 249.512 | 285944 | 2726402.3 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 8 | 2019 | ARP, CSOSG2, MATS | 744 | 76.527 | 0.1823 | 239.254 | 273662.4 | 2609283.4 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 9 | 2019 | ARP, CSOSG2, MATS | 720 | 75.155 | 0.1795 | 244.447 | 283529.5 | 2703364 | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 10 | 2019 | ARP, CSOSG2, MATS | 602.07 | 45.198 | 0.1825 | 155.75 | 178837.038 | 1705158.396 | 744
| AR | Flint Creek Power Plant | 6138 | 1 |  | 11 | 2019 | ARP, CSOSG2, MATS | 354.61 | 26.94 | 0.1619 | 89.603 | 104972.385 | 1000874.265 | 720
| AR | Flint Creek Power Plant | 6138 | 1 |  | 12 | 2019 | ARP, CSOSG2, MATS | 473.73 | 34.985 | 0.1677 | 105.334 | 125250.055 | 1194220.429 | 744
[8 empty] | Total | 11803.63 | [5 empty] | 13896
|  |  | Data obtained from AMPD 7_9_2020 |  |  |  |  | Capacity Factor during baseline | 84.94%
[8 empty] | Average Monthly NOx emission Rate | 0.18577
[8 empty] | Maximum Monthly NOx Emission Rate | 0.2003
[8 empty] | Annual Emissions based on Average Monthly NOx Emission Rate | 2868
General
SWEPCO used a 7% interest rate to annualize total capital investment estimates for the control strategies evaluated. This interest rate is consistent with past cost analyses for regional haze planning and the social cost of rulemaking specified in the EPA Control Cost Manual. However, EPA Region 6 has indicated that DEQ should evaluate costs annualized based on the bank prime rate consistent with EPA Control Cost Manual guidance on private investments. The EPA Control Cost Manual recommends that assessments of private cost “should be prepared using firm-specific nominal interest rates if possible, or the bank prime rate if firm-specific interest rates cannot be estimated or verified.” Therefore, DEQ has calculated the annualized capital costs using the information provided by SWEPCO and a 3.25% interest rate (bank prime rate on July 16, 2020).
SNCR Cost-Effectiveness Calculations
To determine the cost of SNCR for Flint Creek, Trinity Consultants provided escalated costs from a previous analysis. However, the costs estimated in the previous analysis were based on much higher NOx inlet rates (0.33 lb/MMBtu) than the emission baseline used to calculate emission reductions. Therefore, DEQ has calculated revised estimates based on the maximum monthly emission rate (0.20 lb/MMBTU) as the inlet emission rate.
In addition, SWEPCO assumed that there would be no emission reductions because EPA's FIP was based on an estimated controlled emission rate for SNCR and LNB/OFA of 0.20 lb/MMBTU. This value was in the middle of the range (0.18 - 0.23) of expected controlled emission rates provided by a vendor for SNCR plus LNB/OFA. For LNB/OFA alone, the controlled emission rate was estimated at 0.23 lb/MMBTU. This value was in the upper end of the range (0.18 - 0.23) of expected controlled emission rates provided by the vendor for LNB/OFA. In practice, Flint Creek has achieved an even lower emission rate after installation of LNB/OFA (0.20 lb/MMBTU on a maximum month basis and 0.186 lb/MMBTU on an average month basis).
The difference in control efficiency between the two estimated controlled emission rates (LNB/OFA and LNB/OFA/SNCR) is ten percent. Additionally the difference between the maximum monthly NOx emission rate during the baseline (0.20 lb/MMBTU) and the lower range of controlled emission rates provided by the vendor for LNB/OFA/SNCR (0.18 lb/MMBTU) would result in a 10% emission reduction. Therefore, an inlet emission rate of 0.20 lb/MMBTU and a control efficiency of 10% is appropriate to use for determining costs to ensure that the system is adequately sized to accomodate maximum inlet concentrations.
The difference between the average monthly emission rate during the baseline (0.186 lb/MMBTU) and a controlled emission rate of 0.18 lb/MMBTU is 3.22%. Therefore, DEQ estimates that Flint Creek could achieve a 3.22% emission reduction from baseline emissions if SNCR were installed.

## Flint Creek SNCR Cost
SNCR Capital and O&M Cost Estimate for Flint Creek
Technology
SNCR |  | AEP SWEPCO | EPA FIP Analysis | DEQ Analysis
Parameters/Costs | Equation1
Boiler design capacity, mmBtu/hr (QB) | QB | 6324 | 6324 | 6324
Total operating time (top, hrs/yr) | top = CFtotal × 8760 hrs/yr | 7752 | 7752 | 7440.9757
Total Capacity Factor (CFtotal) | CFtotal = CFplant × CFSNCR | 0.92 | 0.92 | 0.84943
Plant Capacity Factor (CFplant) |  | 0.92 | 0.92 | 0.84943
SNCR Capacity Factor (CFSCNR) | CFSNCR = tSNCR/365 | 1 | 1 | 1
Assumed NOx removal efficiency (ηNOx) |  | 35% | 13.04% | 10%
Uncontrolled NOx rate (NOxin, lb/MMBtu, Max Month Basis) |  | 0.33 | 0.23 | 0.2
Electricity Cost (Costelect, $/kwh) |  | 0.05 | 0.05 | 0.05
Water Cost (Costwater, $/gal) |  | 0.00362 | 0.00362 | 0.00362
Coal Cost (Costcoal, $/MMBtu) |  | 2.5 | 2.5 | 2.5
Coal HHV (Btu/lb) |  | 9000 | 9000 | 9000
Cost of Ash Disposal (Cash, $/ton) |  | 9 | 9 | 9
Capital recovery factor (CRF) | CRF = [ I x (1+i)^a]/[(1+i)^a - 1], where I = interest rate, a = equipment life | 0.094393 | 0.080586 | 0.067995
a. Equipment CRF, 20-yr life,7% interest used for AEP SWEPCO b. Equipment CRF, 30-yr life, 7% interest rate used for EPA FIP analysis c. Equipment CRF, 20 years, 3.125% interest rate used for DEQ analysis
Cost Index | 1.5597
a. 2019 Cost Index | 607.5
b. 1998 Cost Index | 389.5
Capital Costs
Direct Capital Cost (A) | DC ($) = ($950/MMBtu) × QB × ((2375 MMBtu/hr/QB)^0.577) × (0.66 + 0.85ηNOx) × (CI2019/CI1998) | 5199783.1903 | 4186110.5738 | 4045784.3099
Indirect Installation Costs ($)
General Facilities | 0.05 × A | 259989.1595 | 209305.5287 | 202289.2155
Engineering and Home Office Fees | 0.10 × A | 519978.319 | 418611.0574 | 404578.431
Process Contingency | 0.05 × A | 259989.1595 | 209305.5287 | 202289.2155
Total Indirect Installation Costs (B) | = General Facilities Cost + Engineering and Home Office Fees + Process Contingency | 1039956.6381 | 837222.1148 | 809156.862
Other Installation Costs ($)
Project Contingency (C) | C = 0.15 × (A + B) | 935960.9742 | 753499.9033 | 728241.1758
Total Plant Cost (D) | D = A + B + C | 7175700.8026 | 5776832.5918 | 5583182.3477
Allowance for Funds During Construction (E) | E = 0 (Assumed for SNCR) | 0 | 0 | 0
Royalty Allowance (F) | F = 0 (Assumed for SNCR) | 0 | 0 | 0
Preproduction Cost (G) | G = 0.02 × (D + E) | 143514.0161 | 115536.6518 | 111663.647
Inventory Capital (H) | H = Volreagent (gal) × Costreagent ($/gal) | 76102 | 8957 | 4988.0479
Costreag, 50% Urea solution ($/gal) |  | 1.5377 | 1.5377 | 1.5377
Volume of Reagent Tank (Volreagent (gal)) | Volreagent (gal) = qsol x days of reagent supply × 24 hr/day | 49416.9825 | 5816.5573 | 3243.7361
Urea solution volumetric flow rate (qsol, gal/hr) | qsol = (msol x 7.481 gal/ft3 )/ρreagent | 147.0744 | 17.3112 | 9.654
Mass flow rate of urea solution (msol, lb/hr) | msol = mreagent/Cureasol | 1395.84 | 164.2954 | 91.6231
Mass flow rate of reagent (mreagent, lb/hr) | mreagent = (NOxin x QB x ηNOx × NSR x Mreagent)/(MNOx x SRT) | 697.92 | 82.1477 | 45.8115
Normalized Stoichiometric Ratio (NSR) | NSR = ([2 × NOxin + 0.7] × ηNOx)/NOxin | 1.43 | 0.65767 | 0.55
Initial Catalyst and Chemicals (I) | I = 0 (Assumed for SNCR due to no catalyst) | 0 | 0 | 0
Total Capital Investment (TCI) (Capital Cost) | TCI = D + E + F + G + H + I | 7395316.8186 | 5901326.2436 | 5699834.0425
Annual Costs ($)
Annual Maintenance Cost (J) | J = 0.015 × TCI | 110929.7523 | 88519.8937 | 85497.5106
Annual Reagent Cost (K) | K = qsol × Costreag × top | 1755781 | 206360.0327 | 110464.117
Annual Electricity Cost (L) | L = P × Costelect × top | 58064 | 18343.6376 | 12804.384
Power (P, kW) | P = (0.47 × NOxin × NSR × QB)/9.5 | 149.8 | 47.3262 | 34.4159
Annual Water Cost (M) | M = qwater × Costwater × top | 18775.3223 | 2209.9447 | 1182.979
Water flowrate for SNCR system (qwater, gal/hr) | qwater = (msol/ρwater) × [(Cureasolstored/Cureasolinj) - 1] | 669.06 | 78.7515 | 43.9176
Annual ΔCoal Cost (N) | N = ΔCoal × Costcoal × top | 109558.0858 | 12895.3822 | 6902.8726
Additional coal required (ΔCoal, MMBtu/hr) | ΔCoal = (Hv × mreagent × [(1/Cureasolinj) - 1])/106 Btu/MMBtu | 5.6532 | 0.6654 | 0.37107
Annual ΔAsh Cost (O) | O = (ΔAsh × Costash × top)/2000 lb/ton | 1643.3713 | 193.4307 | 103.5431
Additional ash generated (ΔAsh , lb/hr) | ΔAsh = (ΔCoal × ashproduct × 106 Btu/MMBtu)/HHV | 47.1096 | 5.545 | 3.0923
Direct Annual Costs (DAC)/Variable O&M | DAC = J + K + L + M + N + O | 2054751.5316 | 328522.3217 | 216955.4064
Indirect Annual Costs (IDAC)/Annualized Capital Cost | IDAC = CFR × TCI | 698065.5913 | 475566.6579 | 387559.6861
Total Annualized Costs (TAC) | TAC = DAC + IDAC | 2752817.1229 | 804088.9796 | 604515.0925
Based on average Annual Emission Rates:
Total Uncontrolled NOx Emissions (tpy) |  | 2868 | 2868 | 2868
Total Uncontrolled NOx Emissions (lb/MMBTU) |  | 0.18577 | 0.18577 | 0.18577
Control Efficiency (average month basis) |  | 3.104% | 3.104% | 3.104%
Post-Control Emissions (tpy) |  | 2778.97 | 2778.97 | 2778.97
Post-Control Emissions (lb/MMBtu) |  | 0.18 | 0.18 | 0.18
Pollutant Removed (tpy) |  | 89.03 | 89.03 | 89.03
Cost Effectiveness ($/ton removed) |  | 30920.1188 | 9031.6667 | 6790.0182
Interest Rate Sensitivity (7%)
| CRF | 0.094393
| Annualized Capital Cost | 538024.0115
| TAC | 754979.4179
| Cost-Effectiveness | 8480.0596

## Flint Creek SCR $ton
|  |  | Total Annual Cost ($2019) |  |  |  |  | Cost-Effectiveness
| Total Capital Investment (2018 dollars) | Annual O&M (2018 Dollars) | interest = 3.25% | interest = 7% | Average Baseline Emission Rate | Controlled Emission Rate | Estimated Annual Emission Reductions | interest = 3.25% | interest = 7%
AEP SWEPCO | 121440000 | 5260000 | 11657667.7054 | 15046412.8424 | 0.186 | 0.055 | 2019.9355 | 5771.307 | 7448.9571
CRF = [ I x (1+i)^a]/[(1+i)^a - 1], where I = interest rate, a = equipment life
| I | 3.25% | bank prime rate 7/10/20
| a | 30
| CRF | 0.052682
CRF = [ I x (1+i)^a]/[(1+i)^a - 1], where I = interest rate, a = equipment life
| I | 7% | social cost of rulemaking
| a | 30
| CRF | 0.080586

## CEPCI Index
Year (n) | CEPCI Index Value | Cost Index Ratio (Value2019/Valuen)
1998 | 389.5 | 1.5597
1999 | 390.6 | 1.5553
2000 | 394.1 | 1.5415
2001 | 394.3 | 1.5407
2002 | 395.6 | 1.5356
2003 | 402 | 1.5112
2004 | 444.2 | 1.3676
2005 | 468.2 | 1.2975
2006 | 499.6 | 1.216
2007 | 525.4 | 1.1563
2008 | 575.4 | 1.0558
2009 | 521.9 | 1.164
2010 | 550.8 | 1.1029
2011 | 585.7 | 1.0372
2012 | 584.6 | 1.0392
2013 | 567.2 | 1.0711
2014 | 576.1 | 1.0545
2015 | 556.8 | 1.0911
2016 | 541.7 | 1.1215
2017 | 567.5 | 1.0705
2018 | 603.1 | 1.0073
2019 | 607.5 | 1