## Read Me
The "IPM WB 1 - 0.65 lb" and the "IPM WB 1 - 2 lb" tabs of this spreadsheet are adapted from the Sargent and Lundy cost algorithms documentation for a SDA FGD installation, as incorporated in version 5.13 of the IPM model. These tabs are used to calculate correction factors to the annualized costs to account for Entergy having costed scrubber systems for the White Bluff units assuming coal with a much higher sulfur content than has historically been burned. The "Source" tab lists the origination of these cost algorithms and other information used in this spreadsheet. These tabs include a further correction recommended on page 2 of the Sargent and Lundy documentation, but not included in the actual cost algorithms - an adjustment to the base absorber island and balance of plant costs due to atmospheric pressure changes with elevation.
Emissions data downloaded from our Air Markets Program Data are included in the "Annual Emissions" and "Monthly Emissions" tabs as an aid in choosing some input values.
The "Entergy Costs" tabs summarizes those costs we propose are either undocumented or disallowed.
The "Cost Effectiveness" tab first applies corrections to the costs in the "Entergy Costs" tab, generated from the information in the "IPM WB 1 - 0.65 lb" and the "IPM WB 1 - 2 lb" tabs. It then calculates the annualized costs for SDA a the White Bluff Units.
See the "AR Cost TSD" file for details on how the above information has been used.
For the IPM tabs, user must have "show objects" selected in Excel's options for the drop down menus to work:

## Source
The "IPM WB 1-2 lb" and the "IPM WB - 0.68 lb" tabs of this spreadsheet are adapted from the Sargent and Lundy cost algorithms documentation for a SDA FGD installation, as incorporated in version 5.13 of the IPM model. These tabs include a further correction recommended on page 2 of the Sargent and Lundy documentation, but not included in the actual cost algorithms - an adjustment to the base absorber island and balance of plant costs due to atmospheric pressure changes with elevation. The documentation for these cost algorithms are present in "IPM Model – Updates to Cost and Performance for APC Technologies, SDA FGD Cost Development Methodology, Final March 2013, Project 12847-002, Systems Research and Applications Corporation, Prepared by Sargent and Lundy."
The elevation adjustment to the base absorber island and balance of plant costs, that is suggested on page 2 of the above documentation, was accomplished by incorporating an atmospheric pressure change with elevation calculation by NASA via http://exploration.grc.nasa.gov/education/rocket/atmosmet.html. It should be noted that in addition to the NASA algorithm, this calculation requires converting the input feet to meters (multiplying elevation*0.3048) and K-Pa to psi (multiplying the calculation by 0.145038).
Emissions data were downloaded from EPA CAMD's website: http://ampd.epa.gov/ampd/
Entergy's SDA costs came from "Revised Bart Five Factor Analysis, White Bluff Steam Electric Station, Redfield, Arkansas (AFIN 35-00110). Appendix A, SDA cost analysis."
The BOP costs are modified based on costs taken from a 2008 S&L quote in the "Entergy Response to EPA Region 6 comments on Entergy White Bluff draft BART Report 06/10/13. Attachment B."

## BOP
Comments
Excluded BOP Costs
Acct. No. | Description | Equipment | Material | Labor | Total
106.1 | Reagent Prep Enclosure | 0 | 195000 | 492000 | 687000
107.1 | Equipment | 7012000 | 0 | 5610000 | 12622000
107.2 | 4200 Ton Limes Storage Silos | 0 | 2428000 | 5038000 | 7520000
107.3 | Enclosed Railcar Unloading Shed | 0 | 200000 | 200000 | 400000
108 | Unit 1 NOx Controls | 3622000 | 1600000 | 3073000 | 8295000
109 | Unit 2 NOx Controls | 3622000 | 1600000 | 3073000 | 8295000
111 | Unit 1 Flue Gas System | 0 | 364000 | 513000 | 877000
111.2 | Paint Chimney | 0 | 0 | 0 | 0 |  |  |  |  | Added "paint chimney" back into BOP costs
112 | Unit 2 Flue Gas System | 0 | 364000 | 513000 | 877000
Totals for Excluded BOP Items |  | 14256000 | 6751000 | 18512000 | 39573000 |  |  |  |  | changed to calculated totals
Totals for all BOP Items Excluding Percentage Costs |  | 45561000 | 35120000 | 80863000
Percentage BOP Items Reduced (%) |  | 31.2899 | 19.2227 | 22.893 | [5 empty] | The material, and labor reduction percentages changed.
ADJUSTED BOP COSTS
|  | ENTERGY |  |  |  | EPA*
ACCT. NO. | DESCRIPTION | ENTERGY TOTAL EQUIPMENT COST | ENTERGY TOTAL MATERIAL COST | ENTERGY TOTAL LABOR COST | ENTERGY TOTAL COST | EPA TOTAL EQUIPMENT COST | EPA TOTAL MATERIAL COST | EPA TOTAL LABOR COST | EPA TOTAL COST
301 | MOBILIZE/DEMOBILIZE @ 1% OF LABOR
301.2 | MOBILIZE/DEMOBILIZE @ 1% OF LABOR |  |  | 710000 | 710000 |  |  | 547481 | 547481
302 | COST DUE TO OVERTIME - 5-10'S
302.2 | COST DUE TO OVERTIME - 5-10'S |  |  | 10363000 | 10363000 |  |  | 7990909.3 | 7990909.3
304 | PER DIEM - @ $10 PER HOUR
304.2 | PER DIEM - @ $10 PER HOUR |  |  | 10257000 | 10257000 |  |  | 7909172.7 | 7909172.7
305 | SPARE PARTS @ 1% OF EQUIPMENT
305.2 | SPARE PARTS @ 1% OF EQUIPMENT | 476000 |  |  | 476000 | 327059.6 |  |  | 327059.6
306 | FREIGHT @ 5% OF MATERIAL
306.4 | FREIGHT @ 5% OF MATERIAL |  | 1756000 |  | 1756000 |  | 1418496.8 |  | 1418496.8
307 | GENERAL & ADMINISTRATIVE (G&A) @ 5% OF MATERIAL AND LABOR
307.5 | GENERAL & ADMINISTRATIVE (G&A) @ 5% OF MATERIAL AND LABOR |  | 1756000 | 3143000 | 4899000 |  | 1418496.8 | 2423567.3 | 3842064.1
307.6 | GENERAL & ADMINISTRATIVE (G&A) @ 5% OF MATERIAL AND LABOR |  |  | 1456000 | 1456000 |  |  | 1122721.6 | 1122721.6
308 | PROFIT @ 10% OF MATERIAL AND LABOR
308.5 | PROFIT @ 10% OF MATERIAL AND LABOR |  | 3512000 | 6285000 | 9797000 |  | 2836993.6 | 4846363.5 | 7683357.1
308.6 | PROFIT @ 10% OF MATERIAL AND LABOR |  |  | 2913000 | 2913000 |  |  | 2246214.3 | 2246214.3
360 | NON CONTRACTOR INDIRECTS
360.8 | ENGINEERING - BOP |  |  | 9855000 | 9855000 |  |  | 7599190.5 | 7599190.5
| TOTALS | 52482000 |  |  |  | 40686667
| REDUCTION IN BOP COSTS | 11795333
* EPA Adjusted BOP costs are calculated by applying the Equipment, Material, and Labor reduction percentages to Entergy's costs, as Entergy's costs are based on Equipment, Material, and Labor totals, and those totals have changed. | [9 empty] | As above, the material, and labor reduction percentages changed so the calculations that depend on them changed.
Alternate BOP Adjustment
Excluded BOP Costs**
Acct. No. | Description | Equipment | Material | Labor | Total
106.1 | Reagent Prep Enclosure | 0 | 0 | 0 | 0
107.1 | Equipment | 0 | 0 | 0 | 0
107.2 | 4200 Ton Limes Storage Silos | 0 | 0 | 0 | 0
107.3 | Enclosed Railcar Unloading Shed | 0 | 0 | 0 | 0
108 | Unit 1 NOx Controls | 3622000 | 1600000 | 3073000 | 8295000 |  |  |  |  | Entergy does not dispute these costs should be disallowed
109 | Unit 2 NOx Controls | 3622000 | 1600000 | 3073000 | 8295000 |  |  |  |  | Entergy does not dispute these costs should be disallowed
111 | Unit 1 Flue Gas System | 0 | 0 | 0 | 0
111.2 | Paint Chimney | 0 | 0 | 0 | 0
112 | Unit 2 Flue Gas System | 0 | 0 | 0 | 0
Totals for Excluded BOP Items |  | 7244000 | 3200000 | 6146000 | 16590000
Totals for all BOP Items Excluding Percentage Costs |  | 45561000 | 35120000 | 80863000
Percentage BOP Items Reduced (%) |  | 15.8996 | 9.1116 | 7.6005 | [5 empty] | The equipment, material, and labor reduction percentages changed.
ADJUSTED BOP COSTS
|  | ENTERGY |  |  |  | EPA*
ACCT. NO. | DESCRIPTION | ENTERGY TOTAL EQUIPMENT COST | ENTERGY TOTAL MATERIAL COST | ENTERGY TOTAL LABOR COST | ENTERGY TOTAL COST | EPA TOTAL EQUIPMENT COST | EPA TOTAL MATERIAL COST | EPA TOTAL LABOR COST | EPA TOTAL COST
301 | MOBILIZE/DEMOBILIZE @ 1% OF LABOR
301.2 | MOBILIZE/DEMOBILIZE @ 1% OF LABOR |  |  | 710000 | 710000 |  |  | 656040 | 656040
302 | COST DUE TO OVERTIME - 5-10'S
302.2 | COST DUE TO OVERTIME - 5-10'S |  |  | 10363000 | 10363000 |  |  | 9575412 | 9575412
304 | PER DIEM - @ $10 PER HOUR
304.2 | PER DIEM - @ $10 PER HOUR |  |  | 10257000 | 10257000 |  |  | 9477468 | 9477468
305 | SPARE PARTS @ 1% OF EQUIPMENT
305.2 | SPARE PARTS @ 1% OF EQUIPMENT | 476000 |  |  | 476000 | 400316 |  |  | 400316
306 | FREIGHT @ 5% OF MATERIAL
306.4 | FREIGHT @ 5% OF MATERIAL |  | 1756000 |  | 1756000 |  | 1596028.4 |  | 1596028.4
307 | GENERAL & ADMINISTRATIVE (G&A) @ 5% OF MATERIAL AND LABOR
307.5 | GENERAL & ADMINISTRATIVE (G&A) @ 5% OF MATERIAL AND LABOR |  | 1756000 | 3143000 | 4899000 |  | 1596028.4 | 2904132 | 4500160.4
307.6 | GENERAL & ADMINISTRATIVE (G&A) @ 5% OF MATERIAL AND LABOR |  |  | 1456000 | 1456000 |  |  | 1345344 | 1345344
308 | PROFIT @ 10% OF MATERIAL AND LABOR
308.5 | PROFIT @ 10% OF MATERIAL AND LABOR |  | 3512000 | 6285000 | 9797000 |  | 3192056.8 | 5807340 | 8999396.8
308.6 | PROFIT @ 10% OF MATERIAL AND LABOR |  |  | 2913000 | 2913000 |  |  | 2691612 | 2691612
360 | NON CONTRACTOR INDIRECTS
360.8 | ENGINEERING - BOP |  |  | 9855000 | 9855000 |  |  | 9106020 | 9106020
| TOTALS | 52482000 |  |  |  | 48347797.6
| REDUCTION IN BOP COSTS | 4134202.4
**Added back in all disputed BOP costs, regardless of whether these costs are disallowed under the CCM or are undocumented.

## Entergy Costs
White Bluff SDA Costs Per Unit* | [6 empty] | Comments
Item | Entergy | EPA Adjustments | EPA (2013) | Comments | Year | CEPCI Annual Composite Index
Total Contractor Costs (2010) | 156974274 |  | 161676662.3824 | Entergy 2010 cost escalated to 2013 | 2008 | 575.4
Contingency (2010) | 20875711 |  | 21501072.713 | EPA escalated to 2013 | 2009 | 521.9
Balance of Plant (2008) | 102085500 | -25684166.5 | 75325819.4205 | S&L 2008 BOP minus EPA adjustments, then escalated to 2013 | 2010 | 550.8 | Updated BOP total from BOP tab, and resulting sums that depend on it.
Balance of Plant Indirect Costs (2012) | 8733104 | -8733104 | 0 | Disallowed or undocumented - see TSD for details | 2011 | 585.7
Misc Contract Labor (2012) | 4583719 | -4583719 | 0 | Disallowed or undocumented - see TSD for details | 2012 | 584.6
Entergy Internal Costs (2012) | 20076644 | -20076644 | 0 | Disallowed or undocumented - see TSD for details | 2013 | 567.3
Capital suspense (2012) | 8348276 | -8348276 | 0 | Disallowed or undocumented - see TSD for details
Total Capital Investment (TCI) |  |  | 258503554.5158
Direct Annual Costs (2008) | 7901369 |  | 7790140.135 | EPA escalated to 2013
Indirect Annual Costs
Overhead (2008) | 2572707 |  | 2536490.5824 | EPA escalated to 2013
Administrative Charges @ 2% of TCI |  |  | 5170071.0903 | 2% of TCI
Property Tax @ 1% of TCI |  |  | 2585035.5452 | 1% of TCI
Insurance @ 1% of TCI |  |  | 2585035.5452 | 1% of TCI
Total Indirect Annual Costs |  |  | 12876632.763
*There is less than a 1% difference between how Entergy calculates the SDA cost for Unit 1 and Unit 2. We therefore ignore this difference in the corrections we make and assume the cost for either unit corresponds to Unit 1.
Alternate White Bluff SDA Costs Per Unit**
Item | Entergy | EPA Adjustments | EPA (2013) | Comments | Year | CEPCI Annual Composite Index
Total Contractor Costs (2010) | 156974274 |  | 161676662.3824 | Entergy 2010 cost escalated to 2013 | 2008 | 575.4
Contingency (2010) | 20875711 |  | 21501072.713 | EPA escalated to 2013 | 2009 | 521.9
Balance of Plant (2008) | 102085500 | -10362101.2 | 90432193.4989 | S&L 2008 BOP minus just NOx controls, then escalated to 2013 | 2010 | 550.8
Balance of Plant Indirect Costs (2012) | 8733104 | 0 | 8474666.2662 | Disallowed costs added back in, then escalated to 2013 | 2011 | 585.7
Misc Contract Labor (2012) | 4583719 | 0 | 4448073.5352 | Disallowed costs added back in, then escalated to 2014 | 2012 | 584.6
Entergy Internal Costs (2012) | 20076644 | 0 | 19482518.2025 | Disallowed costs added back in, then escalated to 2015 | 2013 | 567.3
Capital suspense (2012) | 8348276 | 0 | 8101226.4365 | Disallowed costs added back in, then escalated to 2016
Total Capital Investment (TCI) |  |  | 314116413.0346
Direct Annual Costs (2008) | 7901369 |  | 7790140.135 | EPA escalated to 2013
Indirect Annual Costs
Overhead (2008) | 2572707 |  | 2536490.5824 | EPA escalated to 2013
Administrative Charges @ 2% of TCI |  |  | 6282328.2607 | 2% of TCI
Property Tax @ 1% of TCI |  |  | 3141164.1303 | 1% of TCI
Insurance @ 1% of TCI |  |  | 3141164.1303 | 1% of TCI
Total Indirect Annual Costs |  |  | 15101147.1038
**Added back in all disputed BOP costs, regardless of whether these costs are disallowed under the CCM or are undocumented.

## Cost Effectiveness
White Bluff Unit 1
Item | White Bluff Cost at 2.0 lbs/MMBtu | Ratio of 0.68 lb/MMBtu to 2.0 lb/MMBtu1 | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments | Comments
Annualized Capital Costs | 20831871.7533 | 0.95841 | 19965415.9509 | Using TCI from Entergy Costs tab | Updated totals due to BOP change
Total Direct Annual Costs2 | 7790140.135 | 0.58228 | 4536069.1607 | Sum of direct and indirect costs from Entergy Cost tab
Total Indirect Annual Costs | 12876632.763 | 0.95841 | 12341057.597 |  | Updated to multiply the Total indirect annual costs by 0.9584
Total Annualized Cost |  |  | 36842542.7086
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.65292 | Max monthly value from 2009-2013 for Unit 1
Controlled SO2 Emission Rate (%) |  |  | 90.8106 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 15816.3137 | 3 -yr avg. 2009-2013 for Unit 1, excluding max and min
SO2 Emission Reduction (tons) |  |  | 14362.8851
Cost Effectiveness ($/ton) |  |  | 2565.1213
White Bluff Unit 2
Item |  |  | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Total Annualized Cost |  |  | 36842542.7086 | Assumed same as White Bluff Unit 1
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.67875 | Max monthly value from 2009-2013 for Unit 2
Controlled SO2 Emission Rate (%) |  |  | 91.1602 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 16696.9293 | 3 -yr avg. 2009-2013 for Unit 2, excluding max and min
SO2 Emission Reduction (tons) |  |  | 15220.9606
Cost Effectiveness ($/ton) |  |  | 2420.5136
Independence Unit 1
Item |  |  | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Total Annualized Cost |  |  | 36842542.7086 | Assumed same as White Bluff Unit 1
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.63108 | Max monthly value from 2009-2013 for Unit 1
Controlled SO2 Emission Rate (%) |  |  | 90.4924 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 14268.5767 | 3 -yr avg. 2009-2013 for Unit 1, excluding max and min
SO2 Emission Reduction (tons) |  |  | 12911.9827
Cost Effectiveness ($/ton) |  |  | 2853.3606
Independence Unit 2
Item |  |  | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Total Annualized Cost |  |  | 36842542.7086 | Assumed same as White Bluff Unit 1
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.61151 | Max monthly value from 2009-2013 for Unit 2
Controlled SO2 Emission Rate (%) |  |  | 90.1882 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 15511.4613 | 3 -yr avg. 2009-2013 for Unit 2, excluding max and min
SO2 Emission Reduction (tons) |  |  | 13989.5032
Cost Effectiveness ($/ton) |  |  | 2633.5848
1 Uses the annualized capital and the sum of the fixed and variable operating costs from the "IPM WB 1 - 2 lb" and the "IPM WB 1 - 0.68 lb" tabs.
2 Entergy also includes annualized capital costs as an indirect annual cost, but we separate it out here, as its correction factor is significantly different.
Alternate White Bluff Unit 1
Item | White Bluff Cost at 2.0 lbs/MMBtu | Ratio of 0.68 lb/MMBtu to 2.0 lb/MMBtu1 | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Annualized Capital Costs | 25313512.0103 | 0.95841 | 24260652.2567 | Using TCI from Entergy Costs tab
Total Direct Annual Costs2 | 7790140.135 | 0.58228 | 4536069.1607 | Sum of direct and indirect costs from Entergy Cost tab
Total Indirect Annual Costs | 15101147.1038 | 0.95841 | 14473048.1655
Total Annualized Cost |  |  | 43269769.5829
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.65292 | Max monthly value from 2009-2013 for Unit 1
Controlled SO2 Emission Rate (%) |  |  | 90.8106 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 15816.3137 | 3 -yr avg. 2009-2013 for Unit 1, excluding max and min
SO2 Emission Reduction (tons) |  |  | 14362.8851
Cost Effectiveness ($/ton) |  |  | 3012.6099
Alternate White Bluff Unit 2
Item |  |  | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Total Annualized Cost |  |  | 43269769.5829 | Assumed same as White Bluff Unit 1
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.67875 | Max monthly value from 2009-2013 for Unit 2
Controlled SO2 Emission Rate (%) |  |  | 91.1602 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 16696.9293 | 3 -yr avg. 2009-2013 for Unit 2, excluding max and min
SO2 Emission Reduction (tons) |  |  | 15220.9606
Cost Effectiveness ($/ton) |  |  | 2842.7752
Alternate Independence Unit 1
Item |  |  | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Total Annualized Cost |  |  | 43269769.5829 | Assumed same as White Bluff Unit 1
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.63108 | Max monthly value from 2009-2013 for Unit 1
Controlled SO2 Emission Rate (%) |  |  | 90.4924 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 14268.5767 | 3 -yr avg. 2009-2013 for Unit 1, excluding max and min
SO2 Emission Reduction (tons) |  |  | 12911.9827
Cost Effectiveness ($/ton) |  |  | 3351.1329
Alternate Independence Unit 2
Item |  |  | Corrected White Bluff Cost to 0.68 lbs/MMBtu | Comments
Total Annualized Cost |  |  | 43269769.5829 | Assumed same as White Bluff Unit 1
Interest Rate (%) |  |  | 7
Equipment Lifetime (years) |  |  | 30
Capital Recovery Factor (CRF) |  |  | 0.080586
SO2 Emission Rate (lbs/MMBtu) |  |  | 0.61151 | Max monthly value from 2009-2013 for Unit 2
Controlled SO2 Emission Rate (%) |  |  | 90.1882 | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
SO2 Emission Baseline (tons) |  |  | 15511.4613 | 3 -yr avg. 2009-2013 for Unit 2, excluding max and min
SO2 Emission Reduction (tons) |  |  | 13989.5032
Cost Effectiveness ($/ton) |  |  | 3093.0169

## $ per Deciview
Annualized Costs
Independence Unit 1 | 36842542.7086
Independence Unit 2 | 36842542.7086
Total Cost | 73685085.4172
Control Option | Caney Creek | Upper Buffalo | Hercules Glades | Mingo
∆ Deciview | 1.096 | 1.178 | 1.056 | 1.045
$/Deciview | 67230917.3514 | 62551006.2964 | 69777543.0087 | 70512043.4614

## IPM WB 1 - 2 lb
| Facility | Unit
| White Bluff | 1
[6 empty] | Comments | Potential Facilities to Analyze
| Variable | Designation | Units | Value | Calculation |  | Facility | Unit | MW | Choices for Input Boxes
| Unit Size (Gross) | A | (MW) | 850 | <--- User Input (Greater than 50 MW) |  | Independence | 1 | 850 | Aux Power VOM Possibilities | Include Aux Power in VOM | Don't include Aux Power in VOM
| Retrofit Factor | B |  | 1 | <--- User Input (an "average" retrofit has a factor =1.0) |  |  | 2 | 850 | Type of Coal | BIT | PRB | LIG
| Gross Heat Rate | C | (Btu/kWh) | 10769.9852 | <--- User Input | Max annual value from 2009-2013 | White Bluff | 1 | 850
| SO2 Rate | D | (lb/MMBtu) | 2 | <--- User Input (SDA FGD Estimation only valid up to 3 lb/MMBtu SO2 Rate) | Max monthly value from 2009-2013 |  | 2 | 850
| Type of Coal | E |  | PRB | <--- User Input (PRB, BIT, or LIG)
(Total Capital Investment TCI) | Coal Factor | F |  | 1.05 | Bit=1, PRB=1.05, Lig=1.07
| Heat Rate Factor | G |  | 1.077 | C/10000
| Heat Input | H | (Btu/Hr) | 9154487425.0301 | A*C*1000
| Operating SO2 Removal | J | (%) | 95 | <--- User Input (Used to adjust actual operating costs) | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
| Lime Rate | K | (Ton/Hr) | 13.5124 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 removal)
| Waste Rate | L | (Ton/Hr) | 30.022 | (0.8016*(D^2)+31.1917*D)*A*G/2000 (Based on 95% SO2 removal)
User Input ---> | Include Aux Power in VOM | M | (%) | 1.4873 | (0.000547*D^2+0.00649*D+1.3)*F*G | Assume aux power is included in VOM
| Makeup Water Rate | N | (1000 gph) | 54.3003 | (0.04898*(D^2)+0.5925*D+55.11)*A*F*G/1000
| Lime Cost | P | ($/Ton) | 107 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Waste Disposal Cost | Q | ($/Ton) | 8.58 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Aux Power Cost | R | ($/kWh) | 0.047 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Makeup Water Cost | S | ($/1000[gal]) | 0.92 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Operating Labor Rate | T | ($/hr) | 40 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Elevation adjustment if > 500 Feet |  | (feet) | 0 | <--- User Input (no entry needed if less than 500 feet) | No elevation adjustment needed
| Interest Rate |  | (%) | 7 | <---- User Input
| Equipment Lifetime |  | (years) | 30 | <---- User Input
| Gross Load |  | (MW-hours) | 6275922.12 | <---- User Input | Max annual value from 2009-2013
| SO2 Emission Baseline |  | (tons/year) | N/A | <---- User Input | 3 -yr avg. 2009-2013, excluding max and min
| Capital Cost Calculation |  | Explanation of Calculation |  |  | Comments
Includes: Equipment, installation, buildings, foundations, electrical, and retrofit difficulty
| BMR($) | 89059000 | Base module absorber island cost
| BMF($) | 51531000 | Base module reagent preparation and waste recycle/handling cost
| BMB($) | 123214000 | Base module balance of plant costs (including ID or booster fans, piping, ductwork, electrical, etc.)
| BMBA($) | 123214000 | Adjustment to base module balance of plant costs (including ID or booster fans, piping, ductwork, electrical, etc.), if elevation is greater than 500 feet. See page 2 of the S&L documentation.
| BM($) | 263804000 | Total Base module cost including retrofit factor |  |  | Page 6 of the S&L report gives BM=BMR+BMF+BMW+BMB. BMW appears to be an error (holdover from wet scrubber algorithm), as no formula is given for BMW.
| BM($/kW) | 310.3576 | Base module cost per kW
Total Project Cost
| A1 | 26380000 | Engineering and Construction Mnagement costs
| A2 | 26380000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc.
| A3 | 26380000 | Contractor profit and fees.
| CECC ($) | 342944000 | Capital, engineering and construction cost subtotal |  |  | Excludes Owner's Costs.
| CECC($/kW) | 403.4635 | Capital, engineering and construction cost subtotal per kW |  |  | Excludes Owner's Costs.
| B1 | 17147000 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
| TPC' ($) | 360091000 | Total project cost without AFUDC |  |  | Includes Owner's Costs
| TPC' ($/kw) | 423.6365 | Total project cost per kW without AFUDC |  |  | Includes Owner's Costs
| B2 | 36009000 | AFUDC (Based on a 3 year engineering and construction cycle)
| TPC ($) | 396100000 | Total Project Cost (including AFUDC and owner's costs) |  |  | Includes Owner's Costs and AFUDC
| TPC ($/kW) | 466 | Total Project Cost per kW (including AFUDC and owner's costs) |  |  | Includes Owner's Costs and AFUDC
Fixed O&M Cost
| FOMO ($/kW-yr) | 0.78306 | Fixed O&M additional operating labor costs. Based on eight additional operators.
| FOMM ($/kW-yr) | 4.6554 | Fixed O&M costs for waste disposal
| FOMA ($/kW-yr) | 0.079356 | Fixed O&M additional administrative labor costs
| FOM ($/kW-yr) | 5.5178 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) | 1.701 | Variable O&M costs for lime reagent
| VOMW ($/MWh) | 0.30305 | Variable O&M costs for waste disposal
| VOMP ($/MWh) | 0.69901 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above) |  |  | In the calculation, the factor of "10" results from dividing the conversion from kilo to mega (1000) by 100% , since the input for M is a percentage.
| VOMM ($/MWh) | 0.058772 | Variable O&M costs for makeup water
| VOM ($/MWh) | 2.7618 | Total Variable O&M Costs
Annualization
| Capital, engineering and construction cost | 342944000 | Excludes owner's costs and AFUDC
| Capital Recovery factor | 0.080586
| Annualized capital costs | 27636623.5657
| Variable operating costs | 17332840.037 | VOM*(Gross Load)
| Fixed operating costs | 3953099.9415 | FOM*(Gross Load)*(1000kw/MW)*(8760 hours/year)
| Total annualized costs | 48922563.5443
| SO2 emissions reduction (tons) | N/A | J/(100%)*(SO2 emission baseline)
| $/ton | N/A
21285939.9785

## IPM WB 1 - 0.68 lb
| Facility | Unit
| White Bluff | 1
[6 empty] | Comments | Potential Facilities to Analyze
| Variable | Designation | Units | Value | Calculation |  | Facility | Unit | MW | Choices for Input Boxes
| Unit Size (Gross) | A | (MW) | 850 | <--- User Input (Greater than 50 MW) |  | Independence | 1 | 850 | Aux Power VOM Possibilities | Include Aux Power in VOM | Don't include Aux Power in VOM
| Retrofit Factor | B |  | 1 | <--- User Input (an "average" retrofit has a factor =1.0) |  |  | 2 | 850 | Type of Coal | BIT | PRB | LIG
| Gross Heat Rate | C | (Btu/kWh) | 10769.9852 | <--- User Input | Max annual value from 2009-2013 | White Bluff | 1 | 850
| SO2 Rate | D | (lb/MMBtu) | 0.67875 | <--- User Input (SDA FGD Estimation only valid up to 3 lb/MMBtu SO2 Rate) | Max monthly value from 2009-2013 |  | 2 | 850
| Type of Coal | E |  | PRB | <--- User Input (PRB, BIT, or LIG)
(Total Capital Investment TCI) | Coal Factor | F |  | 1.05 | Bit=1, PRB=1.05, Lig=1.07
| Heat Rate Factor | G |  | 1.077 | C/10000
| Heat Input | H | (Btu/Hr) | 9154487425.0301 | A*C*1000
| Operating SO2 Removal | J | (%) | 91.1602 | <--- User Input (Used to adjust actual operating costs) | Assume 95%. If outlet < 0.06 lbs/MMBtu, then assume % control for 0.06 lbs/MMBtu.
| Lime Rate | K | (Ton/Hr) | 4.3107 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 removal)
| Waste Rate | L | (Ton/Hr) | 9.8597 | (0.8016*(D^2)+31.1917*D)*A*G/2000 (Based on 95% SO2 removal)
User Input ---> | Include Aux Power in VOM | M | (%) | 1.4754 | (0.000547*D^2+0.00649*D+1.3)*F*G | Assume aux power is included in VOM
| Makeup Water Rate | N | (1000 gph) | 53.3812 | (0.04898*(D^2)+0.5925*D+55.11)*A*F*G/1000
| Lime Cost | P | ($/Ton) | 107 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Waste Disposal Cost | Q | ($/Ton) | 8.58 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Aux Power Cost | R | ($/kWh) | 0.047 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Makeup Water Cost | S | ($/1000[gal]) | 0.92 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Operating Labor Rate | T | ($/hr) | 40 | <--- User Input | Entergy from S&L 2008 Wet FGD vs. SDA Cost Analysis
| Elevation adjustment if > 500 Feet |  | (feet) | 0 | <--- User Input (no entry needed if less than 500 feet) | No elevation adjustment needed
| Interest Rate |  | (%) | 7 | <---- User Input
| Equipment Lifetime |  | (years) | 30 | <---- User Input
| Gross Load |  | (MW-hours) | 6275922.12 | <---- User Input | Max annual value from 2009-2013
| SO2 Emission Baseline |  | (tons/year) | N/A | <---- User Input | 3 -yr avg. 2009-2013, excluding max and min
| Capital Cost Calculation |  | Explanation of Calculation |  |  | Comments
Includes: Equipment, installation, buildings, foundations, electrical, and retrofit difficulty
| BMR($) | 88102000 | Base module absorber island cost
| BMF($) | 41515000 | Base module reagent preparation and waste recycle/handling cost
| BMB($) | 123214000 | Base module balance of plant costs (including ID or booster fans, piping, ductwork, electrical, etc.)
| BMBA($) | 123214000 | Adjustment to base module balance of plant costs (including ID or booster fans, piping, ductwork, electrical, etc.), if elevation is greater than 500 feet. See page 2 of the S&L documentation.
| BM($) | 252831000 | Total Base module cost including retrofit factor |  |  | Page 6 of the S&L report gives BM=BMR+BMF+BMW+BMB. BMW appears to be an error (holdover from wet scrubber algorithm), as no formula is given for BMW.
| BM($/kW) | 297.4482 | Base module cost per kW
Total Project Cost
| A1 | 25283000 | Engineering and Construction Mnagement costs
| A2 | 25283000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc.
| A3 | 25283000 | Contractor profit and fees.
| CECC ($) | 328680000 | Capital, engineering and construction cost subtotal |  |  | Excludes Owner's Costs.
| CECC($/kW) | 386.6824 | Capital, engineering and construction cost subtotal per kW |  |  | Excludes Owner's Costs.
| B1 | 16434000 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
| TPC' ($) | 345114000 | Total project cost without AFUDC |  |  | Includes Owner's Costs
| TPC' ($/kw) | 406.0165 | Total project cost per kW without AFUDC |  |  | Includes Owner's Costs
| B2 | 34511000 | AFUDC (Based on a 3 year engineering and construction cycle)
| TPC ($) | 379625000 | Total Project Cost (including AFUDC and owner's costs) |  |  | Includes Owner's Costs and AFUDC
| TPC ($/kW) | 446.6176 | Total Project Cost per kW (including AFUDC and owner's costs) |  |  | Includes Owner's Costs and AFUDC
Fixed O&M Cost
| FOMO ($/kW-yr) | 0.78306 | Fixed O&M additional operating labor costs. Based on eight additional operators.
| FOMM ($/kW-yr) | 4.4617 | Fixed O&M costs for waste disposal
| FOMA ($/kW-yr) | 0.077032 | Fixed O&M additional administrative labor costs
| FOM ($/kW-yr) | 5.3218 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) | 0.5207 | Variable O&M costs for lime reagent
| VOMW ($/MWh) | 0.095502 | Variable O&M costs for waste disposal
| VOMP ($/MWh) | 0.69342 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above) |  |  | In the calculation, the factor of "10" results from dividing the conversion from kilo to mega (1000) by 100% , since the input for M is a percentage.
| VOMM ($/MWh) | 0.057777 | Variable O&M costs for makeup water
| VOM ($/MWh) | 1.3674 | Total Variable O&M Costs
Annualization
| Capital, engineering and construction cost | 328680000 | Excludes owner's costs and AFUDC
| Capital Recovery factor | 0.080586
| Annualized capital costs | 26487139.106
| Variable operating costs | 8581744.2311 | VOM*(Gross Load)
| Fixed operating costs | 3812704.934 | FOM*(Gross Load)*(1000kw/MW)*(8760 hours/year)
| Total annualized costs | 38881588.2712
| SO2 emissions reduction (tons) | N/A | J/(100%)*(SO2 emission baseline)
| $/ton | N/A

## Annual Emissions
Facility Name | Facility ID (ORISPL) | Unit ID | Year | SO2 (tons) |  | SO2 max 2009-2012 (tons) | SO2 avg. 2009-2012 excluding Max and Min (tons) | Avg. NOx Rate (lb/MMBtu) | NOx (tons) | Heat Input (MMBtu) | Operating Time | # of Months Reported | Gross Load (MW-h) | Gross Load avg. (MW-h) | Gross Load Max 2009-2012 (MW-h) | Gross Load avg. 2009-2012 excluding Max and Min (MW-h) | Gross Heat Rate (Btu/kWh) | Gross Heat Rate 2009-2012 Max (Btu/kWh) | Gross Heat Rate 2009-2012 Avg. (Btu/kWh) | Gross Heat Rate avg. 2009-2012 excluding Max and Min (tons) | County | Operating Status | Unit Type | Fuel Type (Primary) | Fuel Type (Secondary) | SO2 Control(s) | NOx Control(s) | PM Control(s) | Facility Latitude | Facility Longitude
Independence | 6641 | 1 | 2009 | 12254.112 |  |  |  | 0.247 | 6610.405 | 53166393.592 | 7333.67 | 12 | 5395291.54 |  |  |  | 9854.2207 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 1 | 2010 | 14916.687 |  |  |  | 0.2449 | 7840.682 | 63712503.744 | 8372.26 | 12 | 6463749.67 |  |  |  | 9856.8953 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 1 | 2011 | 15307.855 |  |  |  | 0.2442 | 7013.311 | 57172444.205 | 7816.33 | 12 | 5805478.47 |  |  |  | 9848.0159 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 1 | 2012 | 16232.508 |  |  |  | 0.1968 | 5364.48 | 55348315.806 | 8481.7 | 12 | 5513571 |  |  |  | 10038.5605 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 1 | 2013 | 12581.188 | 14258.47 | 16232.508 | 14268.5767 | 0.2075 | 4737.474 | 45732632.491 | 7246.08 | 12 | 4847543.25 | 5605126.786 | 6463749.67 | 5571447.0033 | 9434.1876 | 10038.5605 | 9806.376 | 9853.044 | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 2 | 2009 | 15171.182 |  |  |  | 0.2381 | 7727.701 | 64649132.488 | 8169.31 | 12 | 6525058.18 |  |  |  | 9907.8247 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 2 | 2010 | 13757.957 |  |  |  | 0.2461 | 6777.974 | 55125638.276 | 7584.92 | 12 | 5953972.85 |  |  |  | 9258.6311 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 2 | 2011 | 15090.108 |  |  |  | 0.2269 | 6397.368 | 56273139.99 | 8024.15 | 12 | 5693302.45 |  |  |  | 9884.0946 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 2 | 2012 | 16741.242 |  |  |  | 0.2012 | 5702.292 | 57205848.235 | 7404.38 | 12 | 5385122.96 |  |  |  | 10622.9419 |  |  |  | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
Independence | 6641 | 2 | 2013 | 16273.094 | 15406.7166 | 16741.242 | 15511.4613 | 0.207 | 5976.929 | 58742728.755 | 8436.87 | 12 | 6041306.5 | 5919752.588 | 6525058.18 | 5896193.9333 | 9723.5141 | 10622.9419 | 9879.4013 | 9838.4778 | Independence | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 35.6733 | -91.4083
White Bluff | 6009 | 1 | 2009 | 16280.78 |  |  |  | 0.2464 | 6568.524 | 52685717.338 | 7193.29 | 12 | 5408275.96 |  |  |  | 9741.6844 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 1 | 2010 | 15936.257 |  |  |  | 0.2501 | 7926.698 | 63178867.579 | 8004.27 | 12 | 6275922.12 |  |  |  | 10066.8661 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 1 | 2011 | 15018.022 |  |  |  | 0.2733 | 7269.366 | 52436173.444 | 6886.84 | 12 | 4888905.49 |  |  |  | 10725.5445 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 1 | 2012 | 15231.904 |  |  |  | 0.2705 | 6890.792 | 50688511.501 | 7599.14 | 12 | 4710116.35 |  |  |  | 10761.6262 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 1 | 2013 | 17227.069 | 15938.8064 | 17227.069 | 15816.3137 | 0.3039 | 9243.919 | 60158485.036 | 7825.2 | 12 | 5585753.73 | 5373794.73 | 6275922.12 | 5294311.7267 | 10769.9852 | 10769.9852 | 10413.1413 | 10518.0123 | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 2 | 2009 | 17551.02 |  |  |  | 0.2774 | 7954.841 | 56474071.88 | 7610.45 | 12 | 5841825.62 |  |  |  | 9667.1958 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 2 | 2010 | 12528.087 |  |  |  | 0.3099 | 7879.763 | 49581773.28 | 6608.21 | 12 | 5130420.18 |  |  |  | 9664.2715 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 2 | 2011 | 16666.341 |  |  |  | 0.2948 | 8743.32 | 58613642.107 | 7986.23 | 12 | 5937159.33 |  |  |  | 9872.3377 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 2 | 2012 | 16455.26 |  |  |  | 0.2597 | 7344.834 | 56244208.743 | 7596.48 | 12 | 5210328.58 |  |  |  | 10794.7527 |  |  |  | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392
White Bluff | 6009 | 2 | 2013 | 16969.187 | 16033.979 | 17551.02 | 16696.9293 | 0.2934 | 8802.925 | 59297615.241 | 7612.16 | 12 | 5420970.13 | 5508140.768 | 5937159.33 | 5491041.4433 | 10938.5615 | 10938.5615 | 10187.4238 | 10111.4287 | Jefferson | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator | 34.4236 | -92.1392

## Monthly Emissions
Facility Name | Facility ID (ORISPL) | Unit ID | Year | Month | SO2 (tons) | SO2 Rate (lbs/MMBtu) | Avg. Annual SO2 (lbs/MMBtu) | Max. Annual SO2 (lbs/MMBtu) | Avg. NOx Rate (lb/MMBtu) | NOx (tons) | Heat Input (MMBtu) | Operating Time | Gross Load (MW-h) | County | Facility Latitude | Facility Longitude | Owner | Operating Status | Unit Type | Fuel Type (Primary) | Fuel Type (Secondary) | SO2 Control(s) | NOx Control(s) | PM Control(s)
Independence | 6641 | 1 | 2009 | 1 | 1112.151 | 0.46047 |  |  | 0.2352 | 571.803 | 4830465.816 | 687.09 | 490490 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 2 | 877.947 | 0.43075 |  |  | 0.2361 | 486.431 | 4076386.389 | 600.3 | 402233 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 3 | [7 empty] | 0 |  | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 4 | 449.006 | 0.45494 |  |  | 0.2764 | 282.576 | 1973914.516 | 338.89 | 194663 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 5 | 1260.304 | 0.49513 |  |  | 0.2883 | 737.935 | 5090807.427 | 708.13 | 514443 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 6 | 1210.71 | 0.45636 |  |  | 0.2919 | 767.094 | 5305949.14 | 719.12 | 545367 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 7 | 1290.234 | 0.46209 |  |  | 0.2794 | 776.893 | 5584384.1 | 744 | 569295 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 8 | 1043.688 | 0.45415 |  |  | 0.2328 | 567.039 | 4596249.032 | 632.02 | 457649 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 9 | 1246.367 | 0.44721 |  |  | 0.2097 | 581.38 | 5573906.5 | 720 | 567102 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 10 | 1372.692 | 0.48613 |  |  | 0.2162 | 615.559 | 5647456.2 | 744 | 587421 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 11 | 1205.953 | 0.4588 |  |  | 0.2122 | 561.403 | 5257029.2 | 720 | 533305 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2009 | 12 | 1185.059 | 0.45319 | 0.45993 | 0.49513 | 0.2512 | 662.294 | 5229845.272 | 720.12 | 533321 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 1 | 1211.494 | 0.45049 |  |  | 0.2445 | 657.44 | 5378572.9 | 744 | 552014 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 2 | 1062.521 | 0.48871 |  |  | 0.2431 | 536.409 | 4348249.983 | 598.77 | 442146 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 3 | 638.782 | 0.4298 |  |  | 0.2372 | 365.953 | 2972472.112 | 433.87 | 303056 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 4 | 1346.07 | 0.48266 |  |  | 0.2444 | 682.76 | 5577690.9 | 720 | 572458 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 5 | 1505.032 | 0.52237 |  |  | 0.2312 | 669.029 | 5762311.6 | 744 | 583514 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 6 | 1353.957 | 0.46441 |  |  | 0.238 | 697.36 | 5830896.4 | 720 | 586437 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 7 | 1408.698 | 0.48491 |  |  | 0.237 | 692.54 | 5810097.3 | 744 | 585833 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 8 | 1423.37 | 0.49842 |  |  | 0.2473 | 711.128 | 5711492.1 | 744 | 568158 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 9 | 1125.766 | 0.39462 |  |  | 0.2506 | 716.304 | 5705567.2 | 720 | 568443 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 10 | 1268.004 | 0.44343 |  |  | 0.2519 | 719.545 | 5719036 | 744 | 577999 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 11 | 1274.402 | 0.4574 |  |  | 0.2544 | 708.145 | 5572378.316 | 719.68 | 568923 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2010 | 12 | 1298.591 | 0.48785 | 0.46709 | 0.52237 | 0.2565 | 684.068 | 5323738.933 | 739.94 | 554768 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 1 | 1400.366 | 0.54365 |  |  | 0.2675 | 695.042 | 5151723.5 | 670 | 533496 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 2 | 1323.388 | 0.51601 |  |  | 0.2424 | 618.974 | 5129304.3 | 672 | 521526 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 3 | 1313.282 | 0.44529 |  |  | 0.2465 | 728.96 | 5898527 | 744 | 606846 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 4 | 36.311 | 0.44857 |  |  | 0.2237 | 19.233 | 161897.532 | 22.98 | 16746 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 5 | 866.825 | 0.51552 |  |  | 0.2657 | 444.006 | 3362932.134 | 681.15 | 325950 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 6 | 1384.92 | 0.54445 |  |  | 0.2629 | 677.957 | 5087408 | 720 | 523227 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 7 | 1694.416 | 0.57052 |  |  | 0.2621 | 781.962 | 5939947.4 | 744 | 612093 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 8 | 1519.303 | 0.56653 |  |  | 0.249 | 678.294 | 5363510.575 | 679.77 | 552937 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 9 | 1481.506 | 0.53 |  |  | 0.2556 | 719.867 | 5590561.6 | 720 | 567726 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 10 | 1440.146 | 0.53515 |  |  | 0.2256 | 611.851 | 5382187.56 | 698.95 | 538494 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 11 | 1449.819 | 0.56745 |  |  | 0.2192 | 556.556 | 5109985.004 | 719.48 | 509915 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2011 | 12 | 1397.572 | 0.55965 | 0.52857 | 0.57052 | 0.1935 | 480.608 | 4994459.6 | 744 | 496520 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 1 | 1579.628 | 0.60147 |  |  | 0.1825 | 475.724 | 5252548.9 | 744 | 522407 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 2 | 1546.653 | 0.59909 |  |  | 0.1924 | 496.227 | 5163301.5 | 696 | 514511 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 3 | 1423.807 | 0.58677 |  |  | 0.1663 | 404.8 | 4853031.6 | 744 | 477489 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 4 | 679.43 | 0.6221 |  |  | 0.1431 | 157.508 | 2184308.206 | 417.7 | 214666 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 5 | 1688.269 | 0.63108 |  |  | 0.1756 | 471.929 | 5350441.3 | 744 | 517843 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 6 | 1550.274 | 0.58954 |  |  | 0.189 | 496.246 | 5259297.5 | 720 | 501326 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 7 | 1270.094 | 0.58006 |  |  | 0.191 | 405.449 | 4379151.8 | 744 | 403042 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 8 | 1269.23 | 0.56988 |  |  | 0.2117 | 450.814 | 4454379.6 | 744 | 430120 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 9 | 1304.062 | 0.58256 |  |  | 0.2143 | 465.432 | 4476985.7 | 720 | 462666 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 10 | 1436.552 | 0.59653 |  |  | 0.2194 | 516.44 | 4816347.8 | 744 | 504190 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 11 | 1297.028 | 0.54675 |  |  | 0.2369 | 553.92 | 4744502.7 | 720 | 501322 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2012 | 12 | 1187.48 | 0.53805 | 0.58699 | 0.63108 | 0.2177 | 469.993 | 4414019.2 | 744 | 463989 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 1 | 1171.65 | 0.54361 |  |  | 0.199 | 426.186 | 4310666.02 | 696.5 | 450265.35 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 2 | 1004.214 | 0.50844 |  |  | 0.1992 | 392.211 | 3950166.4 | 672 | 421870 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 3 | 1163.73 | 0.54592 |  |  | 0.1936 | 414.457 | 4263385.611 | 694.48 | 448250.75 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 4 | [7 empty] | 0 |  | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 5 | 186.919 | 0.55728 |  |  | 0.1535 | 62.701 | 670820.3 | 152 | 66322 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 6 | 1267.076 | 0.52528 |  |  | 0.2135 | 519.054 | 4824374.462 | 703.37 | 503191.48 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 7 | 1240.603 | 0.53412 |  |  | 0.216 | 504.39 | 4645397.17 | 677.25 | 478085.26 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 8 | 1445.235 | 0.55416 |  |  | 0.2205 | 578.618 | 5215938 | 744 | 540419 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 9 | 1364.337 | 0.56764 |  |  | 0.1979 | 477.191 | 4807090.3 | 720 | 501691 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 10 | 1169.094 | 0.54471 |  |  | 0.195 | 423.152 | 4292506.028 | 722.48 | 462325.41 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 11 | 1154.896 | 0.57493 |  |  | 0.2233 | 422.369 | 4017522.9 | 720 | 443499 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 1 | 2013 | 12 | 1413.434 | 0.59705 | 0.55029 | 0.59705 | 0.2263 | 517.145 | 4734765.3 | 744 | 531624 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 1 | 1276.04 | 0.46195 |  |  | 0.2702 | 744.704 | 5524532.522 | 671.78 | 553203 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 2 | 1050.148 | 0.45194 |  |  | 0.2434 | 573.261 | 4647312.485 | 619.28 | 472513 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 3 | 1259.634 | 0.47102 |  |  | 0.2257 | 618.477 | 5348581.741 | 674.69 | 555996 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 4 | 1422.481 | 0.49474 |  |  | 0.2649 | 763.753 | 5750416.5 | 720 | 595450 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 5 | 1279.792 | 0.49418 |  |  | 0.2754 | 715.907 | 5179504.666 | 654.07 | 521848 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 6 | 1383.57 | 0.46011 |  |  | 0.2548 | 767.844 | 6014051.8 | 720 | 595428 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 7 | 1440.842 | 0.45835 |  |  | 0.2105 | 661.555 | 6287061.2 | 744 | 622058 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 8 | 1475.755 | 0.47804 |  |  | 0.2028 | 630.721 | 6174198.414 | 742.47 | 599027 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 9 | 1276.797 | 0.46089 |  |  | 0.2209 | 606.026 | 5540536.5 | 720 | 552423 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 10 | 759.933 | 0.48591 |  |  | 0.2169 | 356.144 | 3127881.16 | 439.02 | 319684 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 11 | 1289.27 | 0.46474 |  |  | 0.2234 | 622.424 | 5548290.8 | 720 | 564625 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2009 | 12 | 1256.921 | 0.4565 | 0.46986 | 0.49474 | 0.2473 | 666.886 | 5506764.7 | 744 | 572799 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 1 | 1247.003 | 0.44625 |  |  | 0.2367 | 656.146 | 5588853.848 | 742.97 | 571670 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 2 | 1251.072 | 0.53719 |  |  | 0.266 | 613.689 | 4657823.3 | 672 | 535358 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 3 | 1268.88 | 0.48419 |  |  | 0.2893 | 758.129 | 5241212.9 | 744 | 606610 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 4 | 1366.494 | 0.52799 |  |  | 0.2849 | 733.728 | 5176172.5 | 720 | 589684 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 5 | 1547.108 | 0.5828 |  |  | 0.2613 | 688.147 | 5309180.4 | 744 | 602781 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 6 | 1258.444 | 0.51782 |  |  | 0.2444 | 602.166 | 4860567.919 | 639.45 | 526236 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 7 | 1238.534 | 0.50856 |  |  | 0.2172 | 527.766 | 4870785.024 | 641.36 | 503568 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 8 | 1576.356 | 0.51347 |  |  | 0.227 | 695.952 | 6139997 | 744 | 625793 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 9 | 616.404 | 0.38681 |  |  | 0.2332 | 363.548 | 3187147.976 | 405.59 | 322282 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 10 | 103.895 | 0.42432 |  |  | 0.2012 | 57.761 | 489703.459 | 142.75 | 48954 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 11 | 1062.276 | 0.46091 |  |  | 0.2247 | 526.145 | 4609493.65 | 644.8 | 480932 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2010 | 12 | 1221.491 | 0.48911 | 0.48995 | 0.5828 | 0.2219 | 554.796 | 4994700.3 | 744 | 540103 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 1 | 1494.146 | 0.55228 |  |  | 0.2272 | 613.015 | 5410806.679 | 743.73 | 578969 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 2 | 1211.006 | 0.50909 |  |  | 0.2352 | 557.981 | 4757569.6 | 672 | 504825 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 3 | 853.126 | 0.44573 |  |  | 0.2282 | 446.719 | 3828004.251 | 526.73 | 402324 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 4 | 1358.1 | 0.52529 |  |  | 0.2447 | 634.67 | 5170890.1 | 720 | 539242 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 5 | 1016.419 | 0.5166 |  |  | 0.257 | 490.648 | 3935029.2 | 744 | 402603 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 6 | 1232.873 | 0.54416 |  |  | 0.2211 | 509.898 | 4531256.162 | 648.83 | 462015 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 7 | 1718.039 | 0.55914 |  |  | 0.2237 | 690.843 | 6145276.5 | 744 | 619454 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 8 | 1432.63 | 0.56227 |  |  | 0.2163 | 560.607 | 5095895.906 | 724.69 | 510997 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 9 | 511.564 | 0.50777 |  |  | 0.2 | 210.581 | 2014945.841 | 367.17 | 198906 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 10 | 1569.104 | 0.52885 |  |  | 0.2265 | 668.77 | 5934071.6 | 744 | 569538 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 11 | 1515.608 | 0.57383 |  |  | 0.2211 | 584.718 | 5282392.8 | 720 | 509461 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2011 | 12 | 1177.493 | 0.56515 | 0.53251 | 0.57383 | 0.2066 | 428.919 | 4167001.351 | 669 | 394966 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 1 | 1827.9 | 0.60636 |  |  | 0.2014 | 599.385 | 6029073.9 | 744 | 576879 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 2 | 1748.74 | 0.60456 |  |  | 0.2074 | 599.875 | 5785122.3 | 696 | 550729 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 3 | 1719.579 | 0.57552 |  |  | 0.1913 | 569.678 | 5975767.5 | 744 | 547810 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 4 | 1512.493 | 0.6083 |  |  | 0.1751 | 434.374 | 4972848 | 720 | 465121 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 5 | 1972.428 | 0.61151 |  |  | 0.182 | 594.91 | 6451042.3 | 744 | 575963 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 6 | 1806.742 | 0.58156 |  |  | 0.207 | 647.217 | 6213478.4 | 720 | 562803 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 7 | 1679.408 | 0.58838 |  |  | 0.1997 | 568.942 | 5708582.3 | 744 | 525484 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 8 | 1610.537 | 0.57575 |  |  | 0.213 | 574.497 | 5594580.2 | 744 | 524152 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 9 | 1055.899 | 0.56354 |  |  | 0.2345 | 430.239 | 3747364.066 | 502.73 | 361863 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 10 | [7 empty] | 0 |  | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 11 | 547.702 | 0.52463 |  |  | 0.1929 | 209.89 | 2087948.169 | 301.65 | 198343.96 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2012 | 12 | 1259.814 | 0.54302 | 0.58028 | 0.61151 | 0.2143 | 473.287 | 4640041.1 | 744 | 495975 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 1 | 1392.219 | 0.54307 |  |  | 0.1999 | 503.327 | 5127221.5 | 744 | 536713 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 2 | 1083.62 | 0.5087 |  |  | 0.2058 | 424.724 | 4260389.9 | 672 | 444277 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 3 | 1366.027 | 0.5622 |  |  | 0.1981 | 474.221 | 4859616.1 | 744 | 519150 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 4 | 1474.437 | 0.56109 |  |  | 0.1905 | 505.183 | 5255607 | 720 | 554264 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 5 | 1591.26 | 0.59133 |  |  | 0.2034 | 544.128 | 5381978.9 | 744 | 547682 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 6 | 1512.974 | 0.54243 |  |  | 0.2206 | 619.769 | 5578482.271 | 719.61 | 561801.7 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 7 | 1551.065 | 0.55033 |  |  | 0.2132 | 599.551 | 5636875.7 | 744 | 560667 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 8 | 1604.805 | 0.56403 |  |  | 0.2012 | 568.884 | 5690496.9 | 744 | 560760 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 9 | 1360.295 | 0.57881 |  |  | 0.2043 | 474.906 | 4700302.6 | 645 | 475525 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 10 | 840.25 | 0.52565 |  |  | 0.1956 | 311.482 | 3196982.524 | 501.36 | 337871 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 11 | 1160.294 | 0.55606 |  |  | 0.2278 | 438.902 | 4173244.9 | 720 | 437431 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
Independence | 6641 | 2 | 2013 | 12 | 1335.849 | 0.54731 | 0.55258 | 0.59133 | 0.2206 | 511.852 | 4881530.46 | 738.9 | 505164.8 | Independence | 35.6733 | -91.4083 | Arkansas Electric Cooperative Corporation, City of Jonesboro, City of Osceola, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 1 | 1516.251 | 0.62318 |  |  | 0.2558 | 637.02 | 4866147.765 | 685.9 | 478205 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 2 | 1619.073 | 0.64106 |  |  | 0.2605 | 656.625 | 5051215.5 | 672 | 516064 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 3 | 1735.472 | 0.61403 |  |  | 0.2485 | 698.01 | 5652754.6 | 744 | 570515 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 4 | 107.263 | 0.53091 |  |  | 0.257 | 51.473 | 404076.04 | 59.27 | 42221 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 5 | 29.209 | 0.44214 |  |  | 0.1093 | 13.982 | 132124.11 | 78.67 | 10624 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 6 | 1450.129 | 0.60619 |  |  | 0.2303 | 557.277 | 4784377.448 | 690.47 | 494367 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 7 | 1579.439 | 0.61571 |  |  | 0.2409 | 614.384 | 5130500.194 | 719.47 | 531977 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 8 | 1685.807 | 0.61221 |  |  | 0.2545 | 706.241 | 5507306.9 | 739.75 | 568719 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 9 | 1656.138 | 0.61653 |  |  | 0.2739 | 733.549 | 5372461.1 | 720 | 559457 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 10 | 1426.2 | 0.62898 |  |  | 0.2389 | 557.51 | 4534948.182 | 627.31 | 474908 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 11 | 1796.533 | 0.63631 |  |  | 0.2461 | 693.025 | 5646736.3 | 720 | 585573 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2009 | 12 | 1679.265 | 0.59941 | 0.59722 | 0.64106 | 0.2293 | 649.428 | 5603069.199 | 736.45 | 575642 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 1 | 1509.078 | 0.5358 |  |  | 0.2513 | 709.601 | 5633014.045 | 743.04 | 590808 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 2 | 901.91 | 0.50226 |  |  | 0.2592 | 471.517 | 3591434.2 | 466 | 369659 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 3 | 408.786 | 0.44823 |  |  | 0.1765 | 168.179 | 1824009.68 | 254.8 | 181824 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 4 | 1382.853 | 0.50333 |  |  | 0.2221 | 614.441 | 5494781.105 | 710.15 | 566393 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 5 | 1388.487 | 0.45219 |  |  | 0.2515 | 769.323 | 6141226.6 | 744 | 598077 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 6 | 1377.962 | 0.48971 |  |  | 0.2618 | 746.957 | 5627632.549 | 670.28 | 544114 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 7 | 1500.648 | 0.4925 |  |  | 0.2605 | 793.648 | 6094061 | 744 | 599709 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 8 | 1584.477 | 0.52617 |  |  | 0.2513 | 758.661 | 6022655.9 | 744 | 587588 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 9 | 1587.792 | 0.5383 |  |  | 0.2638 | 776.03 | 5899332.1 | 720 | 580151 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 10 | 1578.055 | 0.5257 |  |  | 0.2496 | 745.951 | 6003664.2 | 744 | 588894 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 11 | 1255.062 | 0.49573 |  |  | 0.2536 | 636.304 | 5063472.4 | 720 | 498685 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2010 | 12 | 1461.148 | 0.50527 | 0.50126 | 0.5383 | 0.2555 | 736.086 | 5783583.8 | 744 | 570018 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 1 | 1587.593 | 0.53662 |  |  | 0.2709 | 799.795 | 5916958.746 | 743.98 | 587140 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 2 | 982.144 | 0.56341 |  |  | 0.2775 | 490.832 | 3486453.957 | 500.65 | 335389 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 3 | 1270.075 | 0.65292 |  |  | 0.2687 | 539.945 | 3890420.3 | 489 | 355388 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 4 | 1580.215 | 0.59095 |  |  | 0.2893 | 782.973 | 5348056.73 | 719.07 | 499739 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 5 | 1543.282 | 0.58173 |  |  | 0.2995 | 792.953 | 5305803.2 | 744 | 487116 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 6 | 1736.653 | 0.60493 |  |  | 0.2674 | 766.605 | 5741676.3 | 720 | 527565 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 7 | 1672.263 | 0.56385 |  |  | 0.2612 | 784.819 | 5931632.794 | 697.57 | 542143 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 8 | 1867.673 | 0.57585 |  |  | 0.276 | 892.239 | 6486649.7 | 744 | 596147 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 9 | 1373.896 | 0.5232 |  |  | 0.2721 | 719.153 | 5251862.108 | 677.47 | 489482 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 10 | 335.901 | 0.52668 |  |  | 0.299 | 188.215 | 1275547.28 | 165.4 | 120975 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 11 | [7 empty] | 0 |  | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2011 | 12 | 1068.327 | 0.56211 | 0.57111 | 0.65292 | 0.2415 | 511.837 | 3801112.329 | 685.7 | 347818 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 1 | 1507.886 | 0.60818 |  |  | 0.2607 | 657.587 | 4958721.911 | 732.13 | 462786.04 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 2 | 1521.489 | 0.62067 |  |  | 0.2695 | 647.012 | 4902724.6 | 696 | 461945 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 3 | 1104.203 | 0.59622 |  |  | 0.2636 | 491.815 | 3703987.168 | 661.44 | 341946.6 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 4 | 957.573 | 0.57163 |  |  | 0.2633 | 452.301 | 3350347.088 | 659.6 | 309648.64 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 5 | 1548.122 | 0.60384 |  |  | 0.2796 | 714.671 | 5127575.516 | 743.53 | 481123.03 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 6 | 1509.459 | 0.63416 |  |  | 0.2705 | 641.898 | 4760469.033 | 705.73 | 444149.82 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 7 | 1340.326 | 0.60322 |  |  | 0.266 | 580.624 | 4443899.9 | 744 | 404201 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 8 | 1629.918 | 0.60386 |  |  | 0.2987 | 793.188 | 5398327.8 | 744 | 490920 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 9 | 1731.604 | 0.60856 |  |  | 0.2733 | 773.252 | 5690820.7 | 720 | 526335 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 10 | 706.755 | 0.60547 |  |  | 0.2778 | 325.158 | 2334563.234 | 287.78 | 219543.52 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 11 | 465.97 | 0.54945 |  |  | 0.2384 | 227.945 | 1696145.024 | 245.01 | 160024.34 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2012 | 12 | 1208.599 | 0.55942 | 0.59706 | 0.63416 | 0.2654 | 585.341 | 4320929.527 | 659.92 | 407493.36 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 1 | 1794.41 | 0.6004 |  |  | 0.2972 | 883.636 | 5977385.5 | 744 | 559529 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 2 | 1402.393 | 0.54423 |  |  | 0.3303 | 852.766 | 5153672.1 | 672 | 478900 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 3 | 1639.012 | 0.55987 |  |  | 0.3497 | 1026.115 | 5855004.5 | 744 | 547328 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 4 | 1633.512 | 0.54287 |  |  | 0.3299 | 991.426 | 6018045.385 | 719.97 | 564671.4 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 5 | 1546.625 | 0.55553 |  |  | 0.347 | 972.285 | 5568118.84 | 694.2 | 518674.8 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 6 | 1449.867 | 0.51378 |  |  | 0.2702 | 775.208 | 5643967.276 | 703.83 | 520089.4 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 7 | 1560.741 | 0.5764 |  |  | 0.2643 | 725.287 | 5415518.286 | 689.72 | 496485.4 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 8 | 1855.527 | 0.60692 |  |  | 0.2949 | 897.557 | 6114526.038 | 743.21 | 562640.92 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 9 | 1491.869 | 0.58255 |  |  | 0.2775 | 726.119 | 5121821.514 | 681.45 | 475860.4 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 10 | 666.836 | 0.57907 |  |  | 0.3182 | 374.167 | 2303125.991 | 355.87 | 211839.36 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 11 | 676.484 | 0.59964 |  |  | 0.2751 | 329.379 | 2256296.018 | 377.79 | 205658.97 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 1 | 2013 | 12 | 1509.792 | 0.63825 | 0.57496 | 0.63825 | 0.2846 | 689.974 | 4731003.588 | 699.16 | 444076.08 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 1 | 1405.367 | 0.63883 |  |  | 0.2769 | 644.881 | 4399798.734 | 625.58 | 448201 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 2 | 358.88 | 0.67875 |  |  | 0.2895 | 153.472 | 1057471.22 | 143.6 | 108729 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 3 | 1088.613 | 0.63005 |  |  | 0.2492 | 461.276 | 3455641.6 | 521.3 | 349612 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 4 | 1563.705 | 0.5882 |  |  | 0.2774 | 730.976 | 5316896.4 | 720 | 558089 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 5 | 1484.16 | 0.63813 |  |  | 0.2626 | 616.881 | 4651588.681 | 646.75 | 479860 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 6 | 1498.113 | 0.61512 |  |  | 0.2604 | 643.913 | 4870929.637 | 665.65 | 506771 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 7 | 1708.731 | 0.61686 |  |  | 0.2769 | 773.208 | 5540137.1 | 744 | 572172 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 8 | 1817.626 | 0.62336 |  |  | 0.2606 | 757.379 | 5831737.3 | 744 | 604210 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 9 | 1770.904 | 0.62558 |  |  | 0.3181 | 903.954 | 5661671.1 | 720 | 584005 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 10 | 1848.033 | 0.62609 |  |  | 0.2994 | 885.313 | 5903389.44 | 743.18 | 611654 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 11 | 1770.199 | 0.63729 |  |  | 0.2819 | 780.241 | 5555412.1 | 720 | 579398 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2009 | 12 | 1236.689 | 0.58481 | 0.62526 | 0.67875 | 0.2752 | 603.346 | 4229398.568 | 616.39 | 439122 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 1 | 1427.963 | 0.54403 |  |  | 0.2762 | 732.565 | 5249542.836 | 713.08 | 546835 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 2 | 1268.653 | 0.5011 |  |  | 0.3112 | 787.61 | 5063445.5 | 672 | 535800 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 3 | 1362.467 | 0.47067 |  |  | 0.3404 | 989.55 | 5789463.7 | 744 | 600338 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 4 | 477.879 | 0.51391 |  |  | 0.3052 | 301.585 | 1859766.603 | 268.32 | 192481 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 5 | 1336.226 | 0.46053 |  |  | 0.3465 | 1007.113 | 5803031.4 | 744 | 595498 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 6 | 1432.363 | 0.48421 |  |  | 0.3526 | 1049.932 | 5916346.5 | 720 | 603783 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 7 | 1219.218 | 0.50639 |  |  | 0.2887 | 719.391 | 4815367.552 | 642.14 | 495804 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 8 | 1313.256 | 0.52923 |  |  | 0.27 | 701.983 | 4962848.468 | 694.43 | 511004 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 9 | 1550.079 | 0.54512 |  |  | 0.2947 | 842.231 | 5687084.2 | 720 | 585294 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 10 | 49.938 | 0.57517 |  |  | 0.3061 | 26.78 | 173646.424 | 22.83 | 17651 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 11 | [7 empty] | 0 |  | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2010 | 12 | 1090.046 | 0.51161 | 0.51291 | 0.57517 | 0.3043 | 721.023 | 4261230.097 | 667.41 | 445930 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 1 | 1487.798 | 0.54242 |  |  | 0.3311 | 926.384 | 5485785.5 | 744 | 588318 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 2 | 1379.834 | 0.57091 |  |  | 0.3083 | 752.711 | 4833804.274 | 671.93 | 495548 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 3 | 1472.372 | 0.61522 |  |  | 0.3144 | 754.53 | 4786513.885 | 597.67 | 474527 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 4 | 246.876 | 0.51504 |  |  | 0.2789 | 150.477 | 958671.174 | 198.45 | 91973 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 5 | 1386.974 | 0.58435 |  |  | 0.2838 | 668.545 | 4747093.792 | 743.97 | 484023 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 6 | 1600.865 | 0.59855 |  |  | 0.2733 | 741.175 | 5349135 | 720 | 540111 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 7 | 1599.405 | 0.54466 |  |  | 0.3069 | 916.908 | 5873058.427 | 736.1 | 584267 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 8 | 1742.087 | 0.57267 |  |  | 0.259 | 788.691 | 6084050.65 | 743.9 | 609690 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 9 | 1248.148 | 0.51766 |  |  | 0.2755 | 678.733 | 4822255.225 | 651.9 | 485682 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 10 | 1724.961 | 0.59679 |  |  | 0.2967 | 861.281 | 5780788.2 | 744 | 585757 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 11 | 1407.063 | 0.57927 |  |  | 0.3 | 748.001 | 4858027.68 | 690.31 | 486549 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2011 | 12 | 1369.959 | 0.54423 | 0.56515 | 0.61522 | 0.3005 | 755.883 | 5034458.3 | 744 | 510711 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 1 | 1346.491 | 0.58317 |  |  | 0.2801 | 672.559 | 4617809.821 | 699.96 | 458738.44 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 2 | 1534.891 | 0.60422 |  |  | 0.256 | 650.566 | 5080558.3 | 696 | 497879 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 3 | 728.632 | 0.59169 |  |  | 0.253 | 315.014 | 2462876.57 | 380.63 | 225203.96 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 4 | 124.721 | 0.53693 |  |  | 0.1691 | 46.546 | 464567.086 | 120.34 | 38376.7 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 5 | 1686.215 | 0.59104 |  |  | 0.239 | 681.02 | 5705889.4 | 744 | 527269 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 6 | 1759.433 | 0.61356 |  |  | 0.2677 | 761.941 | 5735117.5 | 720 | 530441 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 7 | 1424.538 | 0.59651 |  |  | 0.2443 | 582.088 | 4776277 | 744 | 422470 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 8 | 1655.262 | 0.59355 |  |  | 0.2422 | 673.469 | 5577534.483 | 717.49 | 497441.91 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 9 | 1684.319 | 0.59002 |  |  | 0.2361 | 684.305 | 5709410.461 | 690.66 | 512090.95 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 10 | 1855.37 | 0.58439 |  |  | 0.2695 | 851.985 | 6349819.2 | 744 | 587676 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 11 | 1583.332 | 0.53937 |  |  | 0.2746 | 803.96 | 5871071.7 | 720 | 547828 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2012 | 12 | 1072.057 | 0.55072 | 0.58126 | 0.61356 | 0.3142 | 621.38 | 3893277.222 | 619.4 | 364913.62 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 1 | 1659.632 | 0.58169 |  |  | 0.3423 | 981.781 | 5706224.5 | 744 | 529371 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 2 | 395.4 | 0.5268 |  |  | 0.3665 | 279.762 | 1501147.138 | 193.42 | 137872.92 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 3 | 469.29 | 0.56942 |  |  | 0.2688 | 240.982 | 1648302.279 | 236.55 | 155712.46 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 4 | 1647.992 | 0.53625 |  |  | 0.2949 | 911.384 | 6146392.7 | 720 | 572664 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 5 | 1678.165 | 0.54524 |  |  | 0.3074 | 946.537 | 6155726.2 | 744 | 563893 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 6 | 1519.066 | 0.50353 |  |  | 0.291 | 876.083 | 6033637.8 | 720 | 540366 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 7 | 1782.523 | 0.56894 |  |  | 0.28 | 879.075 | 6266131 | 744 | 558442 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 8 | 1778.571 | 0.59738 |  |  | 0.2777 | 849.107 | 5954564.225 | 724.25 | 533241.48 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 9 | 1409.555 | 0.56767 |  |  | 0.2543 | 641.934 | 4966135.697 | 640.43 | 447076.6 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 10 | 1531.418 | 0.58073 |  |  | 0.2765 | 753.29 | 5274146.824 | 721.85 | 484689.13 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 11 | 1558.426 | 0.64224 |  |  | 0.3189 | 776.868 | 4853096 | 720 | 450938 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator
White Bluff | 6009 | 2 | 2013 | 12 | 1539.149 | 0.64237 | 0.57185 | 0.64237 | 0.2728 | 666.124 | 4792110.878 | 703.66 | 446703.54 | Jefferson | 34.4236 | -92.1392 | Arkansas Electric Cooperative Corporation, City of Jonesboro, Conway Corporation, Entergy Corporation, West Memphis Utilities | Operating | Tangentially-fired | Coal | Residual Oil |  | Overfire Air | Electrostatic Precipitator